## Read Me
Std140_TF_Results.xlsx
Example results workbook for Section 7 - Building Thermal Envelope Tests Cases 195-995, & 600FF-980FF
This spreadsheet contains the Standard 140, Informative Annex B8, Section B8.1 example results.
See the "Table List" and "Figure List" sheets for a listing of tables and figures and their locations.
This workbook can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab) for instructions and to enter identifying information for your program.
Import your results to sheet "Your Data" (3rd tab); your results will then automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE: (see Std140_TF_Results.docx for spreadsheet navigation)
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results.
"YourData" : For tested program results if doing comparison; see sheet "Adding Results" for instructions.
"Title Page" : Sets headers for tables and charts and provides cover sheet for example results or new comparison results. See instructions there.
"Program List" : Documentation of simulation programs used to produce example results for Standard 140 Informative Annex B8, Section B8.1
"Table List": List of compiled results Tables in workbook with sheet tab locations (for Standard 140, Informative Annex B8, Section B8.1).
"Figure List": List of compiled results Figures in workbook with sheet tab labels (for Standard 140, Informative Annex B8, Section B8.1).
Compiled Example-Results Tables and Figures as follows:
"Tables 1" through "Tables 7" : tables for annual loads, free-float zone temperatures, solar radiation, sky temperatures
"Tables M1" through "Tables M3" : tables for monthly loads
"Fig B8-1" through "Fig B8-59": figures for annual loads, free-float zone temperatures, solar radiation, sky temperatures
"Fig B8-M1" through "Fig B8-M12": figures for monthly loads
"Fig B8-H1" through "Fig B8-H38" : figures for hourly loads, free-float zone temperatures, solar radiation, sky temperatures
"DATA for charts" : Unformatted compiled results for use in charts.
Individual Example Result Worksheets as follows:
"BSIMAC": BSIMAC, Version 9.0.74, submitted by Alec Johannsen Consulting Engineers, South Africa
"CSE": California Simulation Engine, Version 0.861.1, submitted by Big Ladder Software, United States
"DeST": DeST 2.0, Version 20190401, submitted by Southeast University, China and Tsinghua University, China
"EnergyPlus": EnergyPlus, Version 9.0.1, submitted by GARD Analytics, Inc., United States
"ESP-r": ESP-r, Version 13.3, submitted by University of Strathclyde, United Kingdom
"TRNSYS": TRNSYS, Version 18.01.0001, submitted by Transsolar Energietechnik GmbH, Germany
"TestSpecAlt": Tsky alternative values from test spec (Section 7.2.1.1.1.2 and Annex A1, Section A1.1.1.2)
'TestSpecAlt' data applies only for Tsky as shown in Table B8-16 and Figures B8-6, B8-H10, B8-H11.
"K": Spare data entry sheet

## Adding Results
INSTRUCTIONS FOR ADDING NEW RESULTS
New result data can be imported into this workbook (sheet 'YourData', next tab) and will automatically be included in tables and charts.
Import data so that Cell B66 of Std140_TF_Output.xlsx is in B66 of Sheet "YourData"
Check that the first value Annual Heating Load for Case 600 lands in YourData!C70.
Your data will then appear in the rightmost column of each table on sheets "Tables 1" to "Tables 7" and "Tables M1" to "Tables M3".
Charts are also updated with "your data" automatically.
Complete the program information block just below in the cyan highlighted cells.
This information is used for legend titles for the tables and graphs. See "Comparison" setting on sheet 'Title Page'
Program Name and Version (with full build detail):
Tested Program V1.2.3
| Program Version Release Date: | 2020-01-15
| Program Name for Tables and Charts (short): | Tested Prg
| Results Submission Date: | 2020-03-10
Modeler Organization for Titles (long):
Testing Organization
| Modeler Organization for Tables and Charts (short): | Org
| Model / Organization Indentifier for Charts (short): | Tested Prg/Org

## YourData
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Std140_TF_Output.xlsx |  | 2020-01-01
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Section 7
[Note to Users: This file is reorganized since 140-2017. Red text indicates content changes to 140-2017.]
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 7.3
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
| USER NOTE: Paste new data in row 61 and below. | Program Label in C61 flows to data labels in charts and figures. Avoid overwrite or re-enter "='Adding Results'!G24" there.
Version and Date of Results will also transfer from 'Adding Results' sheet.
To print pdf file, see instructions on "Title Page" tab.
Enter identifying information in C61, C62, C63
| Software: | Tested Prg
| Version: | Tested Program V1.2.3
| Date of Results: | 2020-03-10
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.4561 | 5.7898 | 3.198 | Dec | 31 | 24 | 5.609 | Oct | 18 | 14
| 610 | 4.5503 | 4.3067 | 3.202 | Dec | 31 | 24 | 5.344 | Dec | 1 | 14
| 620 | 4.7041 | 3.9441 | 3.248 | Dec | 31 | 24 | 4.236 | Jun | 26 | 17
| 630 | 5.1094 | 2.7113 | 3.254 | Dec | 31 | 24 | 3.631 | Jun | 26 | 17
| 640 | 2.4391 | 5.4123 | 4.3 | Feb | 8 | 9 | 5.495 | Oct | 18 | 14
| 650 | 0 | 4.6284 | 0 |  |  |  | 5.441 | Oct | 18 | 14
| 660 | 3.9479 | 3.132 | 2.863 | Dec | 31 | 24 | 3.435 | Oct | 18 | 14
| 670 | 5.9173 | 6.0068 | 3.878 | Nov | 26 | 7 | 5.941 | Oct | 18 | 14
| 680 | 2.2206 | 6.3952 | 2.087 | Nov | 26 | 7 | 6.028 | Jan | 22 | 14
| 685 | 5.0448 | 8.8005 | 3.226 | Dec | 31 | 24 | 6.288 | Oct | 18 | 14
| 695 | 2.8967 | 9.1015 | 2.093 | Nov | 26 | 7 | 6.618 | Jan | 22 | 14
| 900 | 1.7651 | 2.4606 | 2.672 | Feb | 9 | 6 | 2.818 | Sep | 11 | 14
| 910 | 2.0799 | 1.4444 | 2.692 | Feb | 9 | 6 | 2.136 | Oct | 12 | 15
| 920 | 3.5573 | 2.6701 | 2.748 | Feb | 9 | 6 | 2.909 | Jun | 26 | 17
| 930 | 4.3184 | 1.8013 | 2.781 | Feb | 9 | 6 | 2.436 | Jun | 26 | 18
| 940 | 1.0773 | 2.3783 | 3.479 | Dec | 31 | 9 | 2.818 | Sep | 11 | 14
| 950 | 0 | 0.7509 | 0 |  |  |  | 2.337 | Sep | 11 | 15
| 960 | 3.0413 | 0.813 | 2.298 | Feb | 9 | 6 | 1.358 | Jun | 26 | 16
| 980 | 0.4054 | 3.7848 | 1.646 | Feb | 9 | 6 | 3.157 | Oct | 18 | 14
| 985 | 2.5431 | 6.3195 | 2.678 | Feb | 9 | 6 | 3.516 | Oct | 1 | 14
| 995 | 1.0194 | 7.2301 | 1.697 | Feb | 9 | 6 | 3.643 | Jan | 22 | 15
| 195 | 4.1143 | 0.6299 | 1.733 | Dec | 31 | 24 | 0.977 | Jun | 26 | 17
| 200 | 5.1278 | 0.8345 | 2.185 | Nov | 26 | 7 | 1.222 | Jun | 26 | 17
| 210 | 6.3295 | 0.5009 | 2.504 | Dec | 31 | 24 | 0.909 | Jun | 26 | 18
| 215 | 5.5973 | 0.9223 | 2.407 | Nov | 26 | 7 | 1.345 | Jun | 26 | 17
| 220 | 6.9918 | 0.5591 | 2.734 | Dec | 31 | 24 | 1.018 | Jun | 26 | 18
| 230 | 10.3855 | 0.9645 | 4.207 | Dec | 31 | 24 | 1.732 | Jun | 26 | 17
| 240 | 5.7694 | 0.8915 | 2.556 | Dec | 31 | 24 | 1.195 | Jun | 26 | 18
| 250 | 5.2644 | 3.038 | 2.719 | Dec | 31 | 24 | 2.735 | Sep | 12 | 14
| 270 | 4.6181 | 7.3166 | 2.668 | Dec | 31 | 24 | 6.04 | Jan | 22 | 14
| 280 | 4.9163 | 5.0469 | 2.687 | Dec | 31 | 24 | 4.165 | Jan | 22 | 14
| 290 | 4.7191 | 5.705 | 2.67 | Dec | 31 | 24 | 5.791 | Jan | 22 | 14
| 300 | 4.7466 | 5.0862 | 2.693 | Dec | 31 | 24 | 3.924 | Jun | 26 | 17
| 310 | 5.1592 | 3.5425 | 2.7 | Dec | 31 | 24 | 3.376 | Jun | 26 | 18
| 320 | 3.9635 | 4.8589 | 2.642 | Feb | 9 | 6 | 5.436 | Jan | 22 | 14
| 395 | 5.0113 | 0.0048 | 2.04 | Dec | 31 | 24 | 0.282 | Jun | 14 | 17
| 400 | 6.8634 | 0.0152 | 2.734 | Dec | 31 | 24 | 0.445 | Jun | 26 | 18
| 410 | 8.5515 | 0.0396 | 3.47 | Dec | 31 | 24 | 0.691 | Jun | 26 | 18
| 420 | 7.3346 | 0.117 | 3.292 | Dec | 31 | 24 | 0.886 | Jun | 26 | 18
| 430 | 5.9253 | 0.7501 | 3.283 | Dec | 31 | 24 | 1.677 | Jun | 26 | 16
| 440 | 4.7094 | 3.9235 | 3.227 | Dec | 31 | 24 | 4.184 | Oct | 18 | 14
| 450 | 3.8052 | 6.6733 | 3.036 | Dec | 31 | 24 | 6.399 | Jan | 22 | 14
| 460 | 4.2031 | 6.358 | 3.116 | Dec | 31 | 24 | 6.152 | Jan | 22 | 14
| 470 | 4.0547 | 6.0887 | 3.112 | Dec | 31 | 24 | 5.768 | Jan | 22 | 14
| 800 | 5.4287 | 0.2682 | 2.846 | Feb | 9 | 6 | 1.016 | Aug | 5 | 15
| 810 | 2.5434 | 1.4654 | 2.727 | Feb | 9 | 6 | 2.233 | Sep | 11 | 14
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 24.8 | -13.79 | Feb | 9 | 7 | 64.46 | Oct | 18 | 15
| 900FF | 24.93 | 0.8 | Feb | 9 | 7 | 44.84 | Sep | 12 | 15
| 650FF | 18.71 | -17.47 | Dec | 31 | 24 | 62.99 | Oct | 1 | 15
| 950FF | 14.77 | -13.42 | Dec | 31 | 24 | 37.33 | Sep | 11 | 15
| 680FF | 31.4 | -8.01 | Feb | 9 | 7 | 72.36 | Oct | 18 | 16
| 980FF | 31.56 | 10.44 | Nov | 4 | 7 | 51.03 | Sep | 12 | 15
960
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1663.67
| NORTH | 432.25
| EAST | 1061
| SOUTH | 1381.75
| WEST | 968.92
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 803.14
| 660/South | 443.78
| 670/South | 1037.54
| 620/West | 635.14
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 662.39
| 630/West | 464.21
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -5.27 | -46.97 | Dec | 31 | 23 | 27.28 | Aug | 5 | 11
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 719.33 | 478.98 | 2.999 | 1 | 4 | 5.523 | 22 | 14 | 282.23 | 53.11 | 1.968 | 1 | 7 | 1.932 | 22 | 15
| Feb | 687.11 | 360.93 | 3.13 | 9 | 6 | 4.798 | 15 | 14 | 312.77 | 13.47 | 2.672 | 9 | 6 | 1.03 | 15 | 15
| Mar | 493.74 | 460.76 | 2.274 | 17 | 6 | 4.402 | 24 | 14 | 140.44 | 65.77 | 1.847 | 17 | 6 | 1.637 | 11 | 14
| Apr | 516.41 | 240.77 | 2.408 | 11 | 5 | 3.65 | 12 | 14 | 271.95 | 21.99 | 1.981 | 3 | 3 | 1.073 | 7 | 15
| May | 156.11 | 329.98 | 1.746 | 1 | 4 | 2.899 | 21 | 14 | 35.54 | 107.69 | 1.315 | 1 | 5 | 1.532 | 11 | 14
| Jun | 18.4 | 516.12 | 0.905 | 9 | 5 | 3.22 | 13 | 13 | 0 | 378.33 | 0 |  |  | 1.912 | 14 | 14
| Jul | 18.44 | 517.58 | 0.673 | 26 | 5 | 3.409 | 29 | 14 | 0 | 382.01 | 0 |  |  | 2.022 | 17 | 14
| Aug | 11.83 | 645.94 | 0.624 | 17 | 5 | 4.414 | 27 | 13 | 0 | 517.28 | 0 |  |  | 2.484 | 29 | 14
| Sep | 89.27 | 727.97 | 1.232 | 28 | 24 | 5.18 | 30 | 14 | 0.3 | 500.2 | 0.152 | 29 | 7 | 2.818 | 11 | 14
| Oct | 363.1 | 654.28 | 1.772 | 9 | 6 | 5.609 | 18 | 14 | 81.19 | 292.83 | 1.312 | 7 | 7 | 2.785 | 1 | 14
| Nov | 632.65 | 413.33 | 3.117 | 26 | 7 | 5.407 | 28 | 14 | 308.36 | 70.48 | 2.394 | 26 | 8 | 1.978 | 22 | 14
| Dec | 749.73 | 443.2 | 3.198 | 31 | 24 | 5.45 | 1 | 14 | 332.3 | 57.43 | 2.136 | 31 | 24 | 1.781 | 2 | 15
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -28.23 | 3.69 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -25.06 | 4.43 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -32.9 | 3.9 | -1.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -37.3 | 3.68 | -2.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 1.8 | 1.08 | 1.08 | -33.91 | 3.67 | -3.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63 | 0.35 | 0.82
| 6 | 15 | 7.74 | 7.74 | 88.43 | 25.21 | 25.21 | -34.83 | 3.81 | -1.53 | 0 | 0 | 0 | 4.52 | 2.51 | 5.87 | 14.73 | 8.16 | 19.12
| 7 | 60 | 31.29 | 31.29 | 274.47 | 52.67 | 52.67 | -38.4 | 4.33 | 0.58 | 0 | 0 | 0 | 18.28 | 10.14 | 23.73 | 30.77 | 17.06 | 39.94
| 8 | 111 | 57.48 | 57.21 | 478.01 | 79.43 | 79.43 | -34.25 | 4.4 | 1.48 | 102.66 | 55.83 | 138.34 | 33.58 | 18.62 | 43.59 | 46.4 | 25.73 | 60.24
| 9 | 158 | 82.85 | 80.81 | 669.37 | 170.67 | 101.86 | -36.56 | 4.91 | 2.59 | 317.8 | 174.62 | 404.72 | 48.4 | 26.84 | 62.83 | 65.59 | 36.83 | 91.76
| 10 | 195 | 103.65 | 99.24 | 828.38 | 300.5 | 117.63 | -35.9 | 6.21 | 5.38 | 474.36 | 262.34 | 588.22 | 60.55 | 33.57 | 78.6 | 109.77 | 60.89 | 168.67
| 11 | 263 | 141.61 | 131.23 | 942.66 | 395.15 | 126.77 | -34.42 | 6.98 | 5.35 | 584.18 | 324.52 | 715.67 | 82.73 | 45.87 | 107.39 | 163.45 | 89.22 | 245.12
| 12 | 278 | 150.74 | 138.42 | 1004.97 | 446.05 | 130.34 | -33.59 | 6.27 | 5.17 | 645.24 | 359.54 | 785.88 | 88.06 | 48.83 | 114.31 | 198.86 | 108.09 | 290.49
| 13 | 277 | 150.11 | 142.31 | 1008.22 | 449.13 | 238.63 | -31.77 | 4.19 | 5.59 | 656.08 | 365.78 | 798.34 | 87.69 | 48.62 | 113.83 | 201.2 | 109.34 | 293.36
| 14 | 259 | 139.22 | 139.98 | 954.79 | 405.03 | 475.15 | -33.37 | 3.17 | 4.69 | 614.43 | 341.84 | 750.45 | 81.33 | 45.09 | 105.58 | 169.91 | 92.65 | 253.65
| 15 | 227 | 120.37 | 128.19 | 848.14 | 316.3 | 673.23 | -33.42 | 1.91 | 6.06 | 523.63 | 290.15 | 645.43 | 70.32 | 38.99 | 91.28 | 117.42 | 64.93 | 180.39
| 16 | 181 | 94.26 | 106.06 | 694.98 | 190.37 | 809.49 | -33.79 | 1.12 | 5.02 | 386.38 | 212.98 | 485.29 | 55.07 | 30.53 | 71.48 | 70.22 | 39.48 | 100.66
| 17 | 104 | 53.76 | 59 | 507.45 | 83.16 | 861.93 | -34.31 | 3.29 | 6.46 | 202.53 | 110.56 | 266.37 | 31.4 | 17.41 | 40.77 | 48.58 | 26.94 | 63.06
| 18 | 53 | 27.69 | 27.75 | 303.92 | 56.83 | 806.56 | -36.64 | 3.29 | 5.23 | 17.86 | 9.65 | 24.99 | 16.17 | 8.97 | 21 | 33.2 | 18.41 | 43.1
| 19 | 11 | 5.66 | 5.66 | 111.65 | 29.07 | 588.02 | -36.77 | 2.49 | 4.8 | 0 | 0 | 0 | 3.3 | 1.83 | 4.29 | 16.98 | 9.42 | 22.04
| 20 | 0 | 0 | 0 | 5.02 | 3.02 | 83.7 | -37.18 | 1.99 | 6.07 | 0 | 0 | 0 | 0 | 0 | 0 | 1.76 | 0.98 | 2.29
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -38.24 | 2 | 1.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -39.09 | 1.83 | 1.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -39.08 | 0.95 | 1.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.58 | 0.95 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.1929 | 0.1977 | 1.9142 | 2.7005 | 1.319 | 2.2317 | 1.4288 | 1.1045 | 0 | 0 | 1.2859 | 0.5402 | 0 | 0 | 0 | 0 | 0.0152 | -0.0817 | 0 | -0.1497 | -0.6566 | -0.5978 | 10 | 15.3
| 2 | 2.2442 | 0.7636 | 1.9489 | 2.7803 | 1.4032 | 2.268 | 1.4731 | 1.2124 | 0 | 0 | 1.3787 | 0.6264 | 0 | 0 | 0 | 0 | 0.1171 | -0.0092 | 0 | -0.0838 | -0.5613 | -0.5257 | 10 | 14.67
| 3 | 2.314 | 1.0729 | 1.9975 | 2.8921 | 1.4852 | 2.3285 | 1.5297 | 1.3311 | 0 | 0 | 1.4837 | 0.722 | 0 | 0 | 0 | 0 | 0.2748 | 0.0929 | 0 | 0 | -0.4336 | -0.4303 | 10 | 14.06
| 4 | 2.3793 | 1.2776 | 2.046 | 2.9948 | 1.5523 | 2.3883 | 1.5807 | 1.4429 | 0 | 0.0032 | 1.583 | 0.8112 | 0 | 0 | 0.2699 | 0 | 0.3643 | 0.1575 | 0 | 0 | -0.3378 | -0.357 | 10 | 13.46
| 5 | 2.3696 | 1.3508 | 2.035 | 2.9914 | 1.5549 | 2.3751 | 1.573 | 1.5009 | 0 | 0.1284 | 1.6295 | 0.8516 | 0.1641 | 0 | 0.4714 | 0 | 0.4569 | 0.2286 | 0 | 0 | -0.2314 | -0.2746 | 10 | 13.01
| 6 | 2.4058 | 1.4438 | 2.0704 | 3.0123 | 1.5877 | 2.4092 | 1.5992 | 1.5899 | 0 | 0.2532 | 1.7082 | 0.9206 | 0 | 0 | 0.1898 | 0 | 0.1508 | 0.0287 | 0 | 0 | -0.3252 | -0.3681 | 10 | 12.48
| 7 | 2.4041 | 1.4769 | 2.0715 | 2.996 | 1.5839 | 2.4061 | 1.5913 | 1.6446 | 0 | 0.3395 | 1.7534 | 0.9569 | 0 | 0 | 0 | 0 | -0.2692 | -0.2498 | 0 | -0.0256 | -0.4771 | -0.4955 | 10 | 12.03
| 8 | 1.7593 | 0.8482 | 1.6575 | 2.2917 | 0.9939 | 1.7606 | 0.9986 | 1.4063 | 0 | 0.1423 | 1.5061 | 0.7132 | 0 | 0 | 0 | 0 | -0.6689 | -0.5429 | 0 | -0.1744 | -0.6473 | -0.6322 | 10 | 12.43
| 9 | 0.1724 | 2.0555 | 0.6446 | 0.5202 | 0 | 0.1732 | -0.4912 | 0.736 | 2.0399 | 0 | 0.8278 | 0.0537 | 0 | 0 | 0 | 0 | -1.1141 | -0.8875 | -0.1172 | -0.3505 | -0.8628 | -0.8054 | 20 | 20
| 10 | 0 | 0 | 0 | 0 | -0.2939 | -1.4394 | -2.0518 | 0.0564 | 0.9166 | 0 | 0.1408 | -0.6094 | -0.574 | -0.2135 | -0.6273 | -0.5687 | -1.7944 | -1.4638 | -0.509 | -0.6653 | -1.2269 | -1.1186 | 22.05 | 20
| 11 | -1.4371 | -0.6027 | 0 | -1.0569 | -2.334 | -2.8539 | -3.4656 | 0 | 0.1647 | 0 | -0.5205 | -1.2465 | -1.633 | -1.0738 | -1.8391 | -1.4224 | -2.5603 | -2.1122 | -0.9139 | -0.9954 | -1.6172 | -1.442 | 27 | 20
| 12 | -3.0461 | -2.6254 | -0.7653 | -2.8741 | -3.8374 | -4.0859 | -4.7027 | 0 | 0 | -0.2953 | -1.1878 | -1.8862 | -2.2299 | -1.4995 | -2.5383 | -2.0059 | -3.0351 | -2.6031 | -1.1701 | -1.2254 | -1.8717 | -1.6777 | 27 | 21.61
| 13 | -4.0618 | -3.8107 | -1.695 | -3.9942 | -4.8444 | -4.9249 | -5.5447 | 0 | 0 | -0.9751 | -1.7328 | -2.3996 | -2.6222 | -1.7842 | -3.0027 | -2.4004 | -3.3511 | -2.9348 | -1.3903 | -1.4199 | -2.0835 | -1.8698 | 27 | 23.61
| 14 | -4.0489 | -3.8987 | -1.7558 | -3.771 | -4.9385 | -4.8207 | -5.5477 | 0 | 0 | -1.1313 | -1.8033 | -2.475 | -2.7062 | -1.8732 | -3.1209 | -2.4939 | -3.3925 | -2.9919 | -1.4891 | -1.5019 | -2.1765 | -1.9514 | 27 | 24.4
| 15 | -3.7032 | -3.6131 | -1.596 | -3.3513 | -4.6828 | -4.4203 | -5.234 | -0.0765 | 0 | -1.2608 | -1.851 | -2.5327 | -2.5424 | -1.8252 | -2.9337 | -2.3018 | -3.1967 | -2.7708 | -1.4777 | -1.4628 | -2.1543 | -1.906 | 27 | 24.99
| 16 | -2.8273 | -2.7731 | -1.0834 | -2.4158 | -3.8771 | -3.5118 | -4.392 | -0.0041 | 0 | -1.1496 | -1.6621 | -2.3569 | -2.0971 | -1.5703 | -2.3867 | -1.8774 | -2.74 | -2.336 | -1.327 | -1.3051 | -1.9999 | -1.7491 | 27 | 24.88
| 17 | -1.4778 | -1.445 | -0.2583 | -1.0962 | -2.5774 | -2.1357 | -3.0628 | 0 | 0 | -0.8191 | -1.2508 | -1.9634 | -1.7004 | -1.3145 | -1.8886 | -1.5159 | -2.3384 | -1.9697 | -1.2085 | -1.1872 | -1.8784 | -1.6324 | 27 | 24
| 18 | 0 | 0 | 0 | 0 | -0.7869 | -0.2244 | -1.2487 | 0 | 0 | -0.1928 | -0.5355 | -1.2772 | -1.3143 | -1.0463 | -1.4086 | -1.1695 | -1.9469 | -1.6179 | -1.0665 | -1.0497 | -1.7311 | -1.4933 | 25.44 | 22.09
| 19 | 0 | 0 | 0.1165 | 0.392 | 0 | 0.8852 | -0.1617 | 0 | 0 | 0 | -0.1478 | -0.9071 | -0.925 | -0.7624 | -0.9444 | -0.8365 | -1.5536 | -1.2808 | -0.9133 | -0.9059 | -1.5729 | -1.3478 | 20.92 | 20.82
| 20 | 0.8846 | 0.9017 | 1.0233 | 1.6082 | 0 | 1.5319 | 0.5115 | 0 | 0.0497 | 0 | 0.1325 | -0.6394 | -0.4668 | -0.4028 | -0.4182 | -0.4822 | -1.091 | -0.9222 | -0.7291 | -0.7371 | -1.3833 | -1.1765 | 20 | 20
| 21 | 1.6036 | 1.6121 | 1.5505 | 2.156 | 0 | 1.9636 | 0.9408 | 0 | 0.3385 | 0 | 0.3703 | -0.4299 | -0.1374 | -0.136 | -0.0306 | -0.2317 | -0.7646 | -0.6746 | -0.5886 | -0.6113 | -1.2429 | -1.0536 | 20 | 20
| 22 | 2.054 | 2.0591 | 1.8786 | 2.6283 | 0.6389 | 2.2691 | 1.2618 | 0 | 0.5907 | 0 | 0.6135 | -0.206 | 0 | 0 | 0 | -0.0751 | -0.5568 | -0.515 | -0.4882 | -0.5265 | -1.138 | -0.9667 | 20 | 20
| 23 | 2.2958 | 2.2988 | 2.0521 | 2.8758 | 1.0626 | 2.4257 | 1.4426 | 0.2729 | 0.7754 | 0 | 0.7935 | -0.0414 | 0 | 0 | 0 | 0 | -0.3834 | -0.3792 | -0.3778 | -0.4338 | -1.0238 | -0.8723 | 20 | 20
| 24 | 2.4084 | 0 | 2.1258 | 2.9932 | 1.2955 | 2.4875 | 1.5352 | 0.4632 | 0 | 0 | 0.9337 | 0.0872 | 0 | 0 | 0 | 0 | -0.1929 | -0.2348 | -0.2453 | -0.3246 | -0.8843 | -0.758 | 11.31 | 17.39
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 4.1 | 12.23 | 19.53 | 20.85 | 14.56 | 22.81
| 2 | 2.6 | 11.76 | 18.75 | 20.35 | 12.77 | 22.34
| 3 | 1.2 | 11.24 | 17.57 | 19.46 | 11.04 | 21.83
| 4 | -0.1 | 10.73 | 16.45 | 18.57 | 9.41 | 21.33
| 5 | -1.04 | 10.35 | 15.28 | 17.59 | 8.08 | 20.95
| 6 | -2.03 | 9.88 | 17.18 | 19.17 | 6.74 | 20.51
| 7 | -2.82 | 9.49 | 19.63 | 21 | 5.6 | 20.15
| 8 | -1.13 | 9.96 | 21.35 | 23.08 | 6.7 | 20.58
| 9 | 4.82 | 11.8 | 23.92 | 24.06 | 11.89 | 22.34
| 10 | 12.84 | 13.97 | 27.73 | 25.36 | 19.29 | 24.4
| 11 | 21.68 | 16.24 | 32.5 | 26.83 | 27.85 | 26.55
| 12 | 30.88 | 18.63 | 36.74 | 27.98 | 37.1 | 28.86
| 13 | 39.35 | 20.81 | 40.54 | 29.02 | 45.92 | 30.93
| 14 | 44.4 | 21.7 | 43.25 | 29.73 | 51.95 | 31.79
| 15 | 47.25 | 22.36 | 44.78 | 30.09 | 56.06 | 32.46
| 16 | 47.1 | 22.31 | 44.69 | 30 | 57.31 | 32.45
| 17 | 43.75 | 21.49 | 43.97 | 29.91 | 55.41 | 31.71
| 18 | 36.64 | 19.62 | 42.77 | 29.72 | 49.91 | 29.97
| 19 | 30.13 | 18.41 | 32.62 | 28.49 | 44.61 | 28.83
| 20 | 24.55 | 17.52 | 29.26 | 26.97 | 39.77 | 27.97
| 21 | 19.67 | 16.71 | 26.82 | 25.74 | 35.56 | 27.3
| 22 | 15.29 | 15.88 | 25.42 | 25.18 | 31.44 | 26.55
| 23 | 11.61 | 15.19 | 23.94 | 24.34 | 27.76 | 25.92
| 24 | 8.59 | 14.61 | 22.2 | 23.16 | 24.5 | 25.38
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 2
| 1 | 3
| 2 | 4
| 3 | 17
| 4 | 26
| 5 | 34
| 6 | 50
| 7 | 74
| 8 | 73
| 9 | 99
| 10 | 125
| 11 | 167
| 12 | 202
| 13 | 208
| 14 | 200
| 15 | 263
| 16 | 284
| 17 | 257
| 18 | 317
| 19 | 333
| 20 | 314
| 21 | 307
| 22 | 321
| 23 | 294
| 24 | 279
| 25 | 299
| 26 | 283
| 27 | 299
| 28 | 315
| 29 | 335
| 30 | 370
| 31 | 383
| 32 | 382
| 33 | 383
| 34 | 349
| 35 | 297
| 36 | 238
| 37 | 197
| 38 | 145
| 39 | 85
| 40 | 70
| 41 | 38
| 42 | 22
| 43 | 11
| 44 | 6
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 |  |  | 8760

## Title Page
ASHRAE Standard 140-2023 | To print example results:
Informative Annex B8, Section B8.1 | 1. Select results type in cell B21:
"Example" for Standard 140 Annex B8 Example Results
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF | "Title Page" thru "Figure List"
"Tables 1" thru "Tables M3" (all tables tabs)
"Fig B8-1" thru "Fig B8-H38" (all figures tabs)
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "Adding Results" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Scratch area for Table subtitle 1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Scratch area for Table subtitle 2
Scratch area for chart subtitles
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1 Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF

## Program List
ASHRAE Standard 140-2023
Computer Programs, Program Authors, and Producers of Example Results for
Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
The programs used to generate the example results for Section 7 are described in Table B11-1. Under the "Computer Program" column, the first entry in each cell is the proper program name and version number. The entries in parentheses are the abbreviations for the programs used in the tables and charts of this workbook.
The second column ("Authoring Organization") indicates the national research facility, university,
or industry organization with expertise in building science that wrote the simulation software.
The third column ("Example Results Produced By") indicates the national research facility, university, or industry organization with expertise in building science that performed the simulations. Most of the organizations that performed simulations are members of the development team for the simulation model that they ran.
See Standard 140, Annex B11 for further details.
TABLE B11-1
Computer Programs, Program Authors, and Producers of Example Results
Computer Program (Abbrev.) | Authoring Organization | Example Results Produced by
BSIMAC 9, Version 9.0.74 (BSIMAC) | Alec Johannsen Consulting Engineers, South Africa | Alec Johannsen Consulting Engineers, South Africa
California Simulation Engine, Version 0.861.1 (CSE) | J.R. Barnaby/C.S. Barnaby/Big Ladder Software LLC/Wrightsoft Corp., United States | Big Ladder Software LLC, United States
DeST 2.0, Version 20190401 (DeST) | Tsinghua University, China | Southeast University, China Tsinghua University, China
EnergyPlus, Version 9.0.1 (EnergyPlus) | U.S. Department of Energy, Building Technologies Office, United States | GARD Analytics, Inc., United States
ESP-r, Version 13.3 (ESP-r) | University of Strathclyde, United Kingdom | University of Strathclyde, United Kingdom
TRNSYS, Version 18.01.0001 (TRNSYS) | Transsolar Energietechnik GmbH, Germany; Thermal Energy System Specialists, United States | Transsolar Energietechnik GmbH, Germany
TRNSYS, Versions 17.02.0005 and 18.00.0017 (N/A) | Transsolar Energietechnik GmbH, Germany; Thermal Energy System Specialists, United States | Ecole Polytechnique Montréal, Canadaa,b
a Ecole Polytechnique and GARD also worked on simulations for developing alternative constant interior and exterior surface
coefficients, applying TRNSYS and EnergyPlus, respectively.
b Also checking input files versus the Transsolar participant’s files and vice versa.
Note: Results for “TestSpec-Alt” are shown in Table B8-16 and in Figures B8-6, B8-H10, and B8-H11; contents of tables and figures are further described in sheet tabs labeled "Table List" and "Figure List". “TestSpec-Alt” results are alternative values resulting from optional alternative inputs for sky temperature provided in the test specification (see Section 7.2.1.1.1.2 and Annex A1, Section A1.1.1.2).

## Table List
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B8-1 | Annual Heating Loads | Tables 1 | B7 - N57
| B8-2 | Annual Sensible Cooling Loads |  | B59 - N109
| B8-3 | Annual Hourly Integrated Peak Heating Loads | Tables 2 | B7 - AI57
| B8-4 | Annual Hourly Integrated Peak Sensible Cooling Loads |  | B59 - AI109
| B8-5 | Free-Float Temperature Output |  | B111 - AI145
| B8-6 | Low Mass Basic Sensitivity Tests | Tables 3 | B7 - N58
| B8-7 | High Mass Basic Sensitivity Tests |  | B61 - N112
| B8-8 | Low Mass In-Depth (Cases 195 thru 320) Sensitivity Tests | Tables 4 | B7 - N76
| B8-9 | Low Mass In-Depth (Cases 395 thru 470) Sensitivity Tests | Tables 5 | B7 - N64
| B8-10 | High Mass Basic and In-Depth Sensitivity Tests |  | B67 - N122
| B8-11 | Annual Transmissivity Coefficient of Windows | Tables 6 | B7 - N16
| B8-12 | Annual Shading Coefficient of Window Shading Devices: Overhangs & Fins |  | B18 - N25
| B8-13 | Case 600 Annual Incident Solar Radiation (kWh/m2) |  | B27 - N36
| B8-14 | Case 600 Annual Transmitted Solar Radiation – Unshaded (kWh/m2) |  | B38 - N46
| B8-15 | Case 600 Annual Transmitted Solar Radiation –Shaded (kWh/m2) |  | B48 - N54
| B8-16 | Sky Temperature Output, Case 600 | Tables 7 | B7 - AM15
| B8-M1 | Monthly Heating Loads | Tables M1 | B7 - N36
| B8-M2 | Monthly Sensible Cooling Loads |  | B38 - N67
| B8-M3 | Monthly Hourly Integrated Peak Heating Loads | Tables M2 | B7 - AB36
| B8-M4 | Monthly Hourly Integrated Peak Sensible Cooling Loads |  | B38 - AB67
| B8-M5 | Monthly Load 600-900 Sensitivity Tests | Tables M3 | B7 - N68

## Figure List
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
List of Figures
| Figure | Title | Sheet Tab
| B8-1 | Annual Incident Solar Radiation | Fig B8-1 Ann Incident Solar
| B8-2 | Annual Transmitted Solar Radiation Unshaded | Fig B8-2 Ann SolRad Unshaded
| B8-3 | Annual Transmitted Solar Radiation Shaded | Fig B8-3 Ann SolRad Shaded
| B8-4 | Annual Transmissivity Coefficient of Windows | Fig B8-4 Trans Coeff
(Unshaded Transmitted)/(Incident Solar Radiation)
| B8-5 | Annual Overhang and Fin Shading Coefficients | Fig B8-5 OH&Fin Shade Coeff
(1-(Shaded)/(Unshaded)) Transmitted Solar Radiation
| B8-6 | Average, Minimum and Maximum Sky Temperature, Case 600 | Fig B8-6 Sky Temp
| B8-7 | Basic: Low Mass Annual Heating | Fig B8-7 Lomass Ann Heat
| B8-8 | Basic: Low Mass Annual Sensible Cooling | Fig B8-8 Lomass Ann Cool
| B8-9 | Basic: Low Mass Peak Heating | Fig B8-9 Lomass Peak Heat
| B8-10 | Basic: Low Mass Peak Sensible Cooling | Fig B8-10 Lomass Peak Cool
| B8-11 | Basic: High Mass Annual Heating | Fig B8-11 Himass Ann Heat
| B8-12 | Basic: High Mass Annual Sensible Cooling | Fig B8-12 Himass Ann Cool
| B8-13 | Basic: High Mass Peak Heating | Fig B8-13 Himass Peak Heat
| B8-14 | Basic: High Mass Peak Sensible Cooling | Fig B8-14 Himass Peak Cool
| B8-15 | Basic and In-Depth: South Window (Delta), | Fig B8-15 Delta-S Win-Ann
Annual Heating and Sensible Cooling
| B8-16 | Basic and In-Depth: South Window (Delta), | Fig B8-16 Delta-S Win-Peak
Peak Heating and Sensible Cooling
| B8-17 | Basic: Window Shading and Orientation (Delta), | Fig B8-17 Delta-ShadeOrient-Load
Annual Heating and Sensible Cooling
| B8-18 | Basic: Window Shading and Orientation (Delta), | Fig B8-18 Delta-ShadeOrient-Peak
Peak Heating and Sensible Cooling
| B8-19 | Basic: Thermostat Setback, Vent Cooling, and Sunspace (Delta), | Fig B8-19 Delta-640650960-Load
Annual Heating and Sensible Cooling
| B8-20 | Basic: Thermostat Setback, Vent Cooling, and Sunspace (Delta), | Fig B8-20 Delta-640650960-Peak
Peak Heating and Sensible Cooling
| B8-21 | Basic and In-Depth: Mass Effect (Delta), | Fig B8-21 Delta-Mass Effect-Ann
Annual Heating and Sensible Cooling
| B8-22 | Basic and In-Depth: Mass Effect (Delta), | Fig B8-22 Delta-Mass Effect-Pk
Peak Heating and Sensible Cooling
| B8-23 | Basic: Cases 660 to 695 and 980 to 995 Annual Heating | Fig B8-23 660+ Ann Heat
| B8-24 | Basic: Cases 660 to 695 and 980 to 995 Annual Cooling | Fig B8-24 660+ Ann Cool
| B8-25 | Basic: Cases 660 to 695 and 980 to 995 Peak Heating | Fig B8-25 660+ Peak Heat
| B8-26 | Basic: Cases 660 to 695 and 980 to 995 Peak Cooling | Fig B8-26 660+ Peak Cool
| B8-27 | Basic: Window Types (Delta), Annual Heating and Sensible Cooling | Fig B8-27 Delta-Windows-Load
| B8-28 | Basic: Window Types (Delta), Peak Heating and Sensible Cooling | Fig B8-28 Delta-Windows-Peak
| B8-29 | Basic: Insulation (Delta), Annual Heating and Sensible Cooling | Fig B8-29 Delta-Insul-Load
| B8-30 | Basic: Insulation (Delta), Peak Heating and Sensible Cooling | Fig B8-30 Delta-Insul-Peak
| B8-31 | Basic: Insulation, Mass Effect (Delta), | Fig B8-31 Del-Mass-Ins-Load
Annual Heating and Sensible Cooling
| B8-32 | Basic: Insulation, Mass Effect (Delta), | Fig B8-32 Del-Mass-Ins-Peak
Peak Heating and Sensible Cooling
| B8-33 | Basic: Average Hourly Annual Temperature Free-Float Cases | Fig B8-33 FF Average Temp
| B8-34 | Basic: Maximum Hourly Annual Temperature Free-Float Cases | Fig B8-34 FF Maximum Temp
| B8-35 | Basic: Minimum Hourly Annual Temperature Free-Float Cases | Fig B8-35 FF Minimum Temp
| B8-36 | In-Depth: Low Mass Cases 195 to 250 Annual Heating | Fig B8-36 195to250 Ann Heat
| B8-37 | In-Depth: Low Mass Cases 195 to 250 Annual Sensible Cooling | Fig B8-37 195to250 Ann Cool
| B8-38 | In-Depth: Low Mass Cases 195 to 250 Peak Heating | Fig B8-38 195to250 Peak Heat
| B8-39 | In-Depth: Low Mass Cases 195 to 250 Peak Sensible Cooling | Fig B8-39 195to250 Peak Cool
| B8-40 | In-Depth: Low Mass Cases 270 to 320 Annual Heating | Fig B8-40 270to320 Ann Heat
| B8-41 | In-Depth: Low Mass Cases 270 to 320 Annual Sensible Cooling | Fig B8-41 270to320 Ann Cool
| B8-42 | In-Depth: Low Mass Cases 270 to 320 Peak Heating | Fig B8-42 270to320 Peak Heat
| B8-43 | In-Depth: Low Mass Cases 270 to 320 Peak Sensible Cooling | Fig B8-43 270to320 Peak Cool
| B8-44 | In-Depth: Cases 195 to 220 (Delta) | Fig B8-44 Delta 195to220 Load
Annual Heating and Sensible Cooling
| B8-45 | In-Depth: Cases 195 to 220 (Delta) | Fig B8-45 Delta 195to220 Peak
Peak Heating and Sensible Cooling
| B8-46 | In-Depth: Cases 220 to 270 (Delta) | Fig B8-46 Delta 220to270 Load
Annual Heating and Sensible Cooling
| B8-47 | In-Depth: Cases 220 to 270 (Delta) | Fig B8-47 Delta 220to270 Peak
Peak Heating and Sensible Cooling
| B8-48 | In-Depth: Cases 270 to 320 (Delta) | Fig B8-48 Delta 270to320 Load
Annual Heating and Sensible Cooling
| B8-49 | In-Depth: Cases 270 to 320 (Delta) | Fig B8-49 Delta 270to320 Peak
Peak Sensible Cooling
| B8-50 | In-Depth: Cases 395 to 440, 800, 810 Annual Heating | Fig B8-50 395to440,8n0 Ann Heat
| B8-51 | In-Depth: Cases 395 to 440, 800, 810 Annual Sensible Cooling | Fig B8-51 395to440,8n0 Ann Cool
| B8-52 | In-Depth: Cases 395 to 440, 800, 810 Peak Heating | Fig B8-52 395to440,8n0 Pk Heat
| B8-53 | In-Depth: Cases 395 to 440, 800, 810 Peak Sensible Cooling | Fig B8-53 395to440,8n0 Pk Cool
| B8-54 | In-Depth: Cases 395 to 600, 810 to 900 (Delta) | Fig B8-54 Del 395-600,810,900 Ld
Annual Heating and Sensible Cooling
| B8-55 | In-Depth: Cases 395 to 600, 810 to 900 (Delta) | Fig B8-55 Del 395-600,810,900 Pk
Peak Heating and Sensible Cooling
| B8-56 | In-Depth: Surface Heat Transfer Cases 600, 450, 460, 470 | Fig B8-56 SurfCoefs-Load
Annual Heating and Sensible Cooling
| B8-57 | In-Depth: Surface Heat Transfer Cases 600, 450, 460, 470 | Fig B8-57 SurfCoefs-Peak
Peak Heating and Sensible Cooling
| B8-58 | In-Depth: Surface Heat Transfer Cases 450 to 600 (Delta) | Fig B8-58 SurfHT Delta-Load
Annual Heating and Sensible Cooling
| B8-59 | In-Depth: Surface Heat Transfer Cases 450 to 600 (Delta) | Fig B8-59 SurfHT Delta-Peak
Peak Heating and Sensible Cooling
| B8-M1 | Monthly Heating, Case 600 | Fig B8-M1 MthlyHtg-600
| B8-M2 | Monthly Sensible Cooling, Case 600 | Fig B8-M2 MthlyCtg-600
| B8-M3 | Monthly Peak Heating, Case 600 | Fig B8-M3 MthlyPkHtg-600
| B8-M4 | Monthly Peak Sensible Cooling, Case 600 | Fig B8-M4 MthlyPkClg-600
| B8-M5 | Monthly Heating, Case 900 | Fig B8-M5 MthlyHtg-900
| B8-M6 | Monthly Sensible Cooling, Case 900 | Fig B8-M6 MthlyCtg-900
| B8-M7 | Monthly Peak Heating, Case 900 | Fig B8-M7 MthlyPkHtg-900
| B8-M8 | Monthly Peak Sensible Cooling, Case 900 | Fig B8-M8 MthlyPkClg-900
| B8-M9 | Monthly Heating Sensitivity (Delta), Case 600-900 | Fig B8-M9 Del-MthlyHtg 600-900
| B8-M10 | Monthly Cooling Sensitivity (Delta), Case 600-900 | Fig B8-M10 Del-MthlyCtg 600-900
| B8-M11 | Monthly Peak Heating Sensitivity (Delta), Case 600-900 | Fig B8-M11 Del-MthlyPkH 600-900
| B8-M12 | Monthly Peak Cooling Sensitivity (Delta), Case 600-900 | Fig B8-M12 Del-MthlyPkC 600-900
| B8-H1 | Case 900FF Annual Hourly Temperature Frequency | Fig B8-H1 Hrly-Temp Freq
| B8-H2 | Case 600 Cloudy & Clear Day Hourly Incident Solar | Fig B8-H2 Hrly-IncSol-Horz
Horizontal (Upward) Facing Surface
| B8-H3 | Case 600 Cloudy & Clear Day Hourly Incident Solar | Fig B8-H3 Hrly-IncidentSol-S
South Facing Surface
| B8-H4 | Case 600 Cloudy & Clear Day Hourly Incident Solar | Fig B8-H4 Hrly-IncidentSol-W
West Facing Surface
| B8-H5 | Cases 600, 660, 670 Hourly Transmitted Solar, Clear/Cold Day (Feb 1) | Fig B8-H5 Hrly-TransSol-Feb1
Double-Pane, Low-E, Single-Pane Windows
| B8-H6 | Case 600 Hourly Transmitted Solar, Cloudy Day (May 4) | Fig B8-H6 Hrly-Trans-May4-600
Double-Pane Windows
| B8-H7 | Cases 660,670 Hourly Transmitted Solar, Cloudy Day (May 4) | Fig B8-H7 Hrly-Trans-May4-6670
Low-E and Single-Pane Windows
| B8-H8 | Case 600 Hourly Transmitted Solar, Clear/Hot Day (Jul 14) | Fig B8-H8 Hrly-Trans-Jul14-600
Double-Pane Windows
| B8-H9 | Cases 660, 670 Hourly Transmitted Solar, Clear/Hot Day (Jul 14) | Fig B8-H9 Hrl-Trans-Jul14-6670
Low-E and Single-Pane Windows
| B8-H10 | Hourly Sky Temperatures, Case 600: | Fig B8-H10 Hrly-Tsky-ClearCloud
Clear/Cold, Cloudy Days
| B8-H11 | Hourly Sky Temperatures, Case 600: | Fig B8-H11 Hrly-Tsky-ColdHot
Clear/Cold, Clear/Hot Days
| B8-H12 | Hourly Free-Float Temperatures, | Fig B8-H12 Hrly-FF Temp-ColdDay
Clear Cold Day (Feb 1), Cases 600FF and 900FF
| B8-H13 | Hourly Free-Float Temperatures, | Fig B8-H13 Hrly-FF Temp-HotDay
Clear Hot Day (Jul 14), Cases 650FF and 950FF
| B8-H14 | Hourly Free-Float Temperatures, | Fig B8-H14 Hr-6980FF T-ColdDay
Clear Cold Day (Feb 1), Cases 680FF and 980FF
| B8-H15 | Hourly Loads: Clear Cold Day, Case 600 (Low Mass, Double-Clear Window) | Fig B8-H15 Hrly-600Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H16 | Hourly Loads: Clear Hot Day, Case 600 (Low Mass, Double-Clear Window) | Fig B8-H16 Hrly-600Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H17 | Hourly Loads: Clear Cold Day, Case 640 (Low Mass, Night Setback) | Fig B8-H17 Hrly-640Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H18 | Hourly Conditioned Zone Temperatures, Clear Cold Day, Case 640 | Fig B8-H18 Hrly-640Tzone-Cold
Heating (+), Sensible Cooling (-)
| B8-H19 | Hourly Loads: Clear Cold Day, Case 940 (High Mass, Night Setback) | Fig B8-H19 Hrly-940Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H20 | Hourly Conditioned Zone Temperatures, Clear Cold Day, Case 940 | Fig B8-H20 Hrly-940Tzone-Cold
Heating (+), Sensible Cooling (-)
| B8-H21 | Hourly Loads: Clear Cold Day, Case 660 (Low-E Window) | Fig B8-H21 Hrly-660Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H22 | Hourly Loads: Clear Hot Day, Case 660 (Low-E Window) | Fig B8-H22 Hrly-660Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H23 | Hourly Loads: Clear Cold Day, Case 670 (Single-Pane Window) | Fig B8-H23 Hrly-670Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H24 | Hourly Loads: Clear Hot Day, Case 670 (Single-Pane Window) | Fig B8-H24 Hrly-670Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H25 | Hourly Loads: Clear Cold Day, Case 680 (Insulation) | Fig B8-H25 Hrly-680Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H26 | Hourly Loads: Clear Hot Day, Case 680 (Insulation) | Fig B8-H26 Hrly-680Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H27 | Hourly Loads: Clear Cold Day, Case 685 (20/20 Tstat) | Fig B8-H27 Hrly-685Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H28 | Hourly Loads: Clear Hot Day, Case 685 (20/20 Tstat) | Fig B8-H28 Hrly-685Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H29 | Hourly Loads: Clear Cold Day, Case 695 (20/20, Insulation) | Fig B8-H29 Hrly-695Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H30 | Hourly Loads: Clear Hot Day, Case 695 (20/20, Insulation) | Fig B8-H30 Hrly-695Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H31 | Hourly Loads: Clear Cold Day, Case 900 (High Mass) | Fig B8-H31 Hrly-900Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H32 | Hourly Loads: Clear Hot Day, Case 900 (High Mass) | Fig B8-H32 Hrly-900Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H33 | Hourly Loads: Clear Cold Day, Case 980 (High Mass, Insulation) | Fig B8-H33 Hrly-980Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H34 | Hourly Loads: Clear Hot Day, Case 900 (High Mass, Insulation) | Fig B8-H34 Hrly-980Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H35 | Hourly Loads: Clear Cold Day, Case 985 (High Mass, 20/20 Tstat) | Fig B8-H35 Hrly-985Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H36 | Hourly Loads: Clear Hot Day, Case 985 (High Mass, 20/20 Tstat) | Fig B8-H36 Hrly-985Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H37 | Hourly Loads: Clear Cold Day, Case 995 (High Mass, 20/20, Insulation) | Fig B8-H37 Hrly-995Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H38 | Hourly Loads: Clear Hot Day, Case 995 (High Mass, 20/20, Insulation) | Fig B8-H38 Hrly-995Loads-Hot
Heating (+), Sensible Cooling (-)

## Tables 1
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-1. Annual Heating Loads (MWh)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
[7 empty] | Min | Max | Mean | (Max-Min)/
Case | [9 empty] | Mean** (%)
600 Base Case, South Windows | 4.05 | 3.9928 | 4.047 | 4.3244 | 4.362 | 4.5036 | 3.9928 | 4.5036 | 4.2133 | 12.12% | 4.4561 | ○ | 0 | 0
610 S. Windows + Overhang | 4.163 | 4.0664 | 4.144 | 4.3748 | 4.527 | 4.5921 | 4.0664 | 4.5921 | 4.3112 | 12.19% | 4.5503 | ○ | 1 | 1
620 East & West Windows | 4.37 | 4.0936 | 4.297 | 4.4851 | 4.5143 | 4.719 | 4.0936 | 4.719 | 4.4132 | 14.17% | 4.7041 | ○ | 2 | 2
630 E&W Windows + Overhang & Fins | 4.923 | 4.3559 | 4.677 | 4.7835 | 5.0506 | 5.1386 | 4.3559 | 5.1386 | 4.8214 | 16.23% | 5.1094 | ○ | 3 | 3
640 Case 600 with Htg Temp. Setback | 2.682 | 2.4032 | 2.619 | 2.6618 | 2.6544 | 2.6528 | 2.4032 | 2.682 | 2.6122 | 10.67% | 2.4391 | ○ | 4 | 4
650 Case 600 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ---- | 0 | ○ | 5 | 5
660 Low-E Windows | 3.574 | 3.602 | 3.821 | 3.7067 | 3.787 | 3.7897 | 3.574 | 3.821 | 3.7134 | 6.652% | 3.9479 | 51.38% |  | 6
670 Single-Pane Windows | 5.484 | 5.3002 | 5.573 | 5.6161 | 5.975 | 6.1399 | 5.3002 | 6.1399 | 5.6814 | 14.78% | 5.9173 | ○ |  | 7
680 Case 600 with Increased Insulation | 2.219 | 1.7861 | 1.732 | 2.1797 | 2.1321 | 2.2863 | 1.732 | 2.2863 | 2.0559 | 26.96% | 2.2206 | ○ |  | 8
685 Case 600 with "20/20" Thermostat | 4.532 | 4.5744 | 4.646 | 4.8771 | 4.9035 | 5.0422 | 4.532 | 5.0422 | 4.7625 | 10.71% | 5.0448 | 0.5155% |  | 9
695 Case 685 with Increased Insulation | 2.709 | 2.4153 | 2.385 | 2.8019 | 2.7321 | 2.8917 | 2.385 | 2.8917 | 2.6558 | 19.08% | 2.8967 | 0.9788% |  | 10
900 South Windows | 1.726 | 1.3789 | 1.591 | 1.6637 | 1.5847 | 1.814 | 1.3789 | 1.814 | 1.6264 | 26.75% | 1.7651 | ○ | 6 | 11
910 S. Windows + Overhang | 2.163 | 1.6477 | 1.86 | 1.9557 | 2.0672 | 2.1318 | 1.6477 | 2.163 | 1.9709 | 26.15% | 2.0799 | ○ | 7 | 12
920 East & West Windows | 3.5 | 2.9561 | 3.259 | 3.3365 | 3.2997 | 3.6067 | 2.9561 | 3.6067 | 3.3263 | 19.56% | 3.5573 | ○ | 8 | 13
930 E&W Windows + Overhang & Fins | 4.27 | 3.5236 | 3.933 | 3.9938 | 4.2776 | 4.3841 | 3.5236 | 4.3841 | 4.0637 | 21.17% | 4.3184 | ○ | 9 | 14
940 Case 900 with Htg Temp. Setback | 1.389 | 0.86324 | 1.149 | 1.0674 | 1.0147 | 1.1691 | 0.86324 | 1.389 | 1.1087 | 47.42% | 1.0773 | ○ | 10 | 15
950 Case 900 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ---- | 0 | ○ | 11 | 16
960 Sunspace |  | 2.5221 | 2.771 | 2.689 | 2.6239 | 2.8595 | 2.5221 | 2.8595 | 2.6931 | 12.53% | 3.0413 | 53.86% | 12 | 17
980 Case 900 with Increased Insulation | 0.72 | 0.24577 | 0.266 | 0.41094 | 0.3511 | 0.45047 | 0.24577 | 0.72 | 0.40738 | 116.4% | 0.4054 | ○ |  | 18
985 Case 900 with "20/20" Thermostat | 2.801 | 2.1202 | 2.279 | 2.3693 | 2.2833 | 2.5364 | 2.1202 | 2.801 | 2.3982 | 28.39% | 2.5431 | ○ |  | 19
995 Case 985 with Increased Insulation | 1.33 | 0.75518 | 0.77 | 1.0065 | 0.9048 | 1.077 | 0.75518 | 1.33 | 0.97392 | 59.02% | 1.0194 | ○ |  | 20
195 Solid Conduction | 4.217 | 3.9901 | 4.157 | 4.0696 | 3.9509 | 4.0939 | 3.9509 | 4.217 | 4.0798 | 6.522% | 4.1143 | ○ | 13 | 21
200 Surface Convection (Int & Ext IR="off") | 5.041 | 4.8135 | 5.226 | 5.1054 | 4.9204 | 5.1429 | 4.8135 | 5.226 | 5.0415 | 8.183% | 5.1278 | ○ | 14 | 22
210 Infrared Radiation (Int IR="off", Ext IR="on") | 5.627 | 5.9663 | 6.531 | 6.0466 | 6.3171 | 6.4295 | 5.627 | 6.531 | 6.1529 | 14.69% | 6.3295 | ○ | 15 | 23
215 Infrared Radiation (Int IR="on", Ext IR="off") | 5.652 | 5.3066 | 5.697 | 5.4054 | 5.1811 | 5.4434 | 5.1811 | 5.697 | 5.4476 | 9.47% | 5.5973 | ○ | 16 | 24
220 In-Depth Base Case | 6.377 | 6.6663 | 7.178 | 6.4551 | 6.7257 | 6.8678 | 6.377 | 7.178 | 6.7117 | 11.93% | 6.9918 | ○ | 17 | 25
230 Infiltration | 9.851 | 9.8124 | 10.417 | 9.9299 | 9.9385 | 10.2343 | 9.8124 | 10.417 | 10.0305 | 6.028% | 10.3855 | ○ | 18 | 26
240 Internal Gains | 5.116 | 5.4426 | 5.944 | 5.2794 | 5.5393 | 5.6572 | 5.116 | 5.944 | 5.4964 | 15.06% | 5.7694 | ○ | 19 | 27
250 Exterior Shortwave Absorptance | 4.733 | 5.0438 | 5.373 | 4.8991 | 4.935 | 5.1047 | 4.733 | 5.373 | 5.0148 | 12.76% | 5.2644 | ○ | 20 | 28
270 South Solar Windows |  | 4.3465 | 4.273 | 4.3854 | 4.5764 | 4.6312 | 4.273 | 4.6312 | 4.4425 | 8.062% | 4.6181 | ○ | 21 | 29
280 Cavity Albedo |  | 4.5249 | 4.619 | 4.5701 | 4.7381 | 4.8699 | 4.5249 | 4.8699 | 4.6644 | 7.396% | 4.9163 | 13.45% | 22 | 30
290 South Shading |  | 4.4242 | 4.381 | 4.4244 | 4.7447 | 4.7248 | 4.381 | 4.7447 | 4.5398 | 8.011% | 4.7191 | ○ | 23 | 31
300 East/West Window |  | 4.3184 | 4.46 | 4.4245 | 4.6679 | 4.7256 | 4.3184 | 4.7256 | 4.5193 | 9.012% | 4.7466 | 5.149% | 24 | 32
310 East/West Shading |  | 4.5803 | 4.846 | 4.6912 | 5.2396 | 5.1626 | 4.5803 | 5.2396 | 4.9039 | 13.44% | 5.1592 | ○ | 25 | 33
320 Thermostat |  | 3.6775 | 3.599 | 3.7712 | 3.9699 | 4.0311 | 3.599 | 4.0311 | 3.8097 | 11.34% | 3.9635 | ○ | 26 | 34
395 Low Mass Solid Conduction | 4.565 | 4.855 | 5.145 | 4.6412 | 4.8657 | 4.9081 | 4.565 | 5.145 | 4.83 | 12.01% | 5.0113 | ○ | 27 | 35
400 Low Mass High Cond. Wall Elements | 5.906 | 6.5358 | 7.047 | 6.3478 | 6.61 | 6.7692 | 5.906 | 7.047 | 6.536 | 17.46% | 6.8634 | ○ | 28 | 36
410 Low Mass Infiltration | 7.63 | 8.0451 | 8.661 | 8.0803 | 8.2122 | 8.4449 | 7.63 | 8.661 | 8.1789 | 12.61% | 8.5515 | ○ | 29 | 37
420 Low Mass Internal Gains | 6.399 | 6.8345 | 7.433 | 6.9058 | 7.027 | 7.2364 | 6.399 | 7.433 | 6.9726 | 14.83% | 7.3346 | ○ | 30 | 38
430 Low Mass Ext. Shortwave Absorptance | 5.171 | 5.454 | 5.954 | 5.6201 | 5.5449 | 5.8505 | 5.171 | 5.954 | 5.5991 | 13.98% | 5.9253 | ○ | 31 | 39
440 Low Mass Cavity Albedo |  | 4.1559 | 4.33 | 4.5001 | 4.5039 | 4.7207 | 4.1559 | 4.7207 | 4.4421 | 12.71% | 4.7094 | ○ | 32 | 40
450 Constant Interior and Exterior Surf Coeffs | 3.743 | 3.9904 | 3.375 | 3.9625 | 3.8503 | 3.8709 | 3.375 | 3.9904 | 3.7987 | 16.2% | 3.8052 | ○ |  | 41
460 Constant Interior Surface Coefficients | 3.828 | 4.0555 | 3.873 | 4.1938 | 4.2625 | 4.2898 | 3.828 | 4.2898 | 4.0838 | 11.31% | 4.2031 | ○ |  | 42
470 Constant Exterior Surface Coefficients | 4.042 | 3.8995 | 3.54 | 4.0939 | 3.9597 | 4.0746 | 3.54 | 4.0939 | 3.9349 | 14.08% | 4.0547 | ○ |  | 43
800 High Mass High Cond. Wall Elements | 5.141 | 4.9057 | 5.403 | 5.1156 | 4.9798 | 5.3695 | 4.9057 | 5.403 | 5.1524 | 9.652% | 5.4287 | 5.168% | 33 | 44
810 High Mass Cavity Albedo |  | 2.0375 | 2.454 | 2.3418 | 2.185 | 2.6098 | 2.0375 | 2.6098 | 2.3256 | 24.61% | 2.5434 | ○ | 34 | 45
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-2. Annual Sensible Cooling Loads (MWh)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
[7 empty] | Min | Max | Mean | (Max-Min)/
Case | [9 empty] | Mean** (%)
600 Base Case, South Windows | 5.822 | 5.9131 | 5.432 | 6.027 | 6.1618 | 5.7795 | 5.432 | 6.1618 | 5.8559 | 12.46% | 5.7898 | ○
610 S. Windows + Overhang | 4.299 | 4.3818 | 4.173 | 4.3328 | 4.2325 | 4.1168 | 4.1168 | 4.3818 | 4.256 | 6.226% | 4.3067 | ○
620 East & West Windows | 4.404 | 4.0793 | 3.909 | 4.0595 | 4.2457 | 3.8407 | 3.8407 | 4.404 | 4.0897 | 13.77% | 3.9441 | ○
630 E&W Windows + Overhang & Fins | 3.074 | 3.0204 | 2.787 | 2.836 | 2.5953 | 2.5729 | 2.5729 | 3.074 | 2.8143 | 17.81% | 2.7113 | ○
640 Case 600 with Htg Temp. Setback | 5.804 | 5.6439 | 5.237 | 5.7631 | 5.8926 | 5.4772 | 5.237 | 5.8926 | 5.6363 | 11.63% | 5.4123 | ○
650 Case 600 with Night Ventilation | 4.629 | 4.6539 | 4.186 | 4.8168 | 4.9451 | 4.6323 | 4.186 | 4.9451 | 4.6438 | 16.35% | 4.6284 | ○
660 Low-E Windows | 3.014 | 3.3397 | 3.26 | 3.2315 | 3.2186 | 2.9663 | 2.9663 | 3.3397 | 3.1717 | 11.77% | 3.132 | ○
670 Single-Pane Windows | 6.539 | 6.5777 | 5.954 | 6.6227 | 6.5203 | 6.1978 | 5.954 | 6.6227 | 6.4019 | 10.45% | 6.0068 | ○
680 Case 600 with Increased Insulation | 5.938 | 6.4298 | 5.932 | 6.4439 | 6.5294 | 6.3098 | 5.932 | 6.5294 | 6.2638 | 9.537% | 6.3952 | ○
685 Case 600 with "20/20" Thermostat | 9.13 | 8.8592 | 8.238 | 9.1188 | 9.1214 | 8.8513 | 8.238 | 9.13 | 8.8864 | 10.04% | 8.8005 | ○
695 Case 685 with Increased Insulation | 8.755 | 8.9741 | 8.386 | 9.1716 | 9.149 | 9.0391 | 8.386 | 9.1716 | 8.9125 | 8.814% | 9.1015 | ○
900 South Windows | 2.714 | 2.4638 | 2.383 | 2.4887 | 2.4877 | 2.2671 | 2.2671 | 2.714 | 2.4674 | 18.11% | 2.4606 | ○
910 S. Windows + Overhang | 1.484 | 1.4149 | 1.49 | 1.3835 | 1.2829 | 1.1909 | 1.1909 | 1.49 | 1.3744 | 21.77% | 1.4444 | ○
920 East & West Windows | 3.128 | 2.7892 | 2.706 | 2.7308 | 2.8144 | 2.5489 | 2.5489 | 3.128 | 2.7862 | 20.79% | 2.6701 | ○
930 E&W Windows + Overhang & Fins | 2.161 | 2.075 | 1.908 | 1.9191 | 1.6538 | 1.6718 | 1.6538 | 2.161 | 1.8981 | 26.72% | 1.8013 | ○
940 Case 900 with Htg. Temp. Setback | 2.613 | 2.3966 | 2.343 | 2.4244 | 2.4276 | 2.2035 | 2.2035 | 2.613 | 2.4013 | 17.05% | 2.3783 | ○
950 Case 900 with Night Ventilation | 0.586 | 0.59803 | 0.618 | 0.70692 | 0.656 | 0.64162 | 0.586 | 0.70692 | 0.63443 | 19.06% | 0.7509 | 36.37%
960 Sunspace |  | 0.92578 | 0.909 | 0.90712 | 0.9496 | 0.78896 | 0.78896 | 0.9496 | 0.89609 | 17.93% | 0.813 | ○
980 Case 900 with Increased Insulation | 3.501 | 3.9953 | 3.758 | 3.7118 | 3.7745 | 3.5185 | 3.501 | 3.9953 | 3.7099 | 13.32% | 3.7848 | ○
985 Case 900 with "20/20" Thermostat | 7.273 | 6.2336 | 5.88 | 6.3592 | 6.2493 | 6.1135 | 5.88 | 7.273 | 6.3514 | 21.93% | 6.3195 | ○
995 Case 985 with Increased Insulation | 7.482 | 7.2022 | 6.771 | 7.2029 | 7.1488 | 7.0638 | 6.771 | 7.482 | 7.1451 | 9.951% | 7.2301 | ○
195 Solid Conduction | 0.712 | 0.60552 | 0.628 | 0.61152 | 0.611 | 0.59153 | 0.59153 | 0.712 | 0.6266 | 19.23% | 0.6299 | ○
200 Surface Convection (Int & Ext IR="off") | 0.839 | 0.80024 | 0.835 | 0.81408 | 0.8004 | 0.78844 | 0.78844 | 0.839 | 0.81286 | 6.22% | 0.8345 | ○
210 Infrared Radiation (Int IR="off", Ext IR="on") | 0.688 | 0.50307 | 0.496 | 0.5599 | 0.5185 | 0.45918 | 0.45918 | 0.688 | 0.53744 | 42.58% | 0.5009 | ○
215 Infrared Radiation (Int IR="on", Ext IR="off") | 0.952 | 0.94579 | 0.922 | 0.87747 | 0.8948 | 0.85047 | 0.85047 | 0.952 | 0.90709 | 11.19% | 0.9223 | ○
220 In-Depth Base Case | 0.803 | 0.6106 | 0.55 | 0.6099 | 0.5762 | 0.49766 | 0.49766 | 0.803 | 0.60789 | 50.23% | 0.5591 | ○
230 Infiltration | 1.184 | 0.99134 | 0.929 | 0.99121 | 0.955 | 0.89664 | 0.89664 | 1.184 | 0.9912 | 28.99% | 0.9645 | ○
240 Internal Gains | 1.287 | 0.98237 | 0.876 | 0.97875 | 0.9218 | 0.83378 | 0.83378 | 1.287 | 0.97995 | 46.25% | 0.8915 | ○
250 Exterior Shortwave Absorptance | 3.612 | 3.429 | 3.471 | 3.1816 | 3.4668 | 2.9038 | 2.9038 | 3.612 | 3.344 | 21.18% | 3.038 | ○
270 South Solar Windows |  | 7.2708 | 6.698 | 7.5215 | 7.3086 | 7.2885 | 6.698 | 7.5215 | 7.2175 | 11.41% | 7.3166 | ○
280 Cavity Albedo |  | 4.9963 | 4.215 | 5.1829 | 5.2058 | 4.8081 | 4.215 | 5.2058 | 4.8816 | 20.3% | 5.0469 | ○
290 South Shading |  | 5.6097 | 5.31 | 5.7425 | 5.3206 | 5.4612 | 5.31 | 5.7425 | 5.4888 | 7.88% | 5.705 | ○
300 East/West Window |  | 5.0551 | 4.805 | 5.152 | 5.0381 | 4.913 | 4.805 | 5.152 | 4.9926 | 6.951% | 5.0862 | ○
310 East/West Shading |  | 3.7519 | 3.402 | 3.6695 | 3.1279 | 3.3242 | 3.1279 | 3.7519 | 3.4551 | 18.06% | 3.5425 | ○
320 Thermostat |  | 4.8585 | 4.42 | 4.986 | 4.9131 | 4.7877 | 4.42 | 4.986 | 4.7931 | 11.81% | 4.8589 | ○
395 Low Mass Solid Conduction | 0.021 | 0.007762 | 0.006 | 0.01038 | 0.0055 | 0.0035162 | 0.0035162 | 0.021 | 0.0090264 | 193.7% | 0.0048 | ○
400 Low Mass High Cond. Wall Elements | 0.063 | 0.023304 | 0.017 | 0.030566 | 0.0244 | 0.012683 | 0.012683 | 0.063 | 0.028492 | 176.6% | 0.0152 | ○
410 Low Mass Infiltration | 0.096 | 0.048491 | 0.041 | 0.057269 | 0.0523 | 0.03512 | 0.03512 | 0.096 | 0.05503 | 110.6% | 0.0396 | ○
420 Low Mass Internal Gains | 0.228 | 0.14062 | 0.119 | 0.15257 | 0.1419 | 0.10944 | 0.10944 | 0.228 | 0.14859 | 79.79% | 0.117 | ○
430 Low Mass Ext. Shortwave Absorptance | 1.084 | 0.90616 | 0.944 | 0.85562 | 0.9527 | 0.73902 | 0.73902 | 1.084 | 0.91358 | 37.76% | 0.7501 | ○
440 Low Mass Cavity Albedo |  | 3.9853 | 3.458 | 4.085 | 4.4141 | 3.7412 | 3.458 | 4.4141 | 3.9367 | 24.29% | 3.9235 | ○
450 Constant Interior and Exterior Surf Coeffs | 6.172 | 5.689 | 6.161 | 6.5073 | 6.6132 | 6.5307 | 5.689 | 6.6132 | 6.2789 | 14.72% | 6.6733 | 6.503%
460 Constant Interior Surface Coefficients | 6.26 | 5.9398 | 5.929 | 6.4746 | 6.7291 | 6.2434 | 5.929 | 6.7291 | 6.2626 | 12.78% | 6.358 | ○
470 Constant Exterior Surface Coefficients | 5.987 | 5.6439 | 5.649 | 6.0294 | 6.0054 | 6.0559 | 5.6439 | 6.0559 | 5.8951 | 6.989% | 6.0887 | 7.964%
800 High Mass High Cond. Wall Elements | 0.473 | 0.37983 | 0.362 | 0.37353 | 0.3914 | 0.28208 | 0.28208 | 0.473 | 0.37697 | 50.65% | 0.2682 | -7.271%
810 High Mass Cavity Albedo |  | 1.4807 | 1.357 | 1.5078 | 1.6056 | 1.2945 | 1.2945 | 1.6056 | 1.4491 | 21.47% | 1.4654 | ○
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 2
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-3. Annual Hourly Integrated Peak Heating Loads
Simulation Model: | BSIMAC |  |  |  | CSE |  |  |  | DeST |  |  |  | EnergyPlus |  |  |  | ESP-r |  |  |  | TRNSYS |  |  |  | Example Result Statistics |  |  |  |  | Tested Prg
[25 empty] | Min | Max | Mean | (Max-Min)/
Case | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | kW | kW | Mean** (%) | kW | Mo. | Day | Hr
600 Base Case, South Windows | 3.255 | Nov | 26 | 8 | 3.0202 | Jan | 1 | 1 | 3.035 | Jan | 1 | 0 | 3.2044 | Dec | 31 | 24 | 3.228 | Jan | 1 | 1 | 3.3589 | Jan | 1 | 1 | 3.0202 | 3.3589 | 3.1836 | 10.64% | 3.198 | Dec | 31 | 24 | ○ | 0 | 0
610 S. Windows + Overhang | 3.166 | Nov | 26 | 8 | 3.0208 | Jan | 1 | 1 | 3.039 | Jan | 1 | 0 | 3.1918 | Dec | 31 | 24 | 3.233 | Jan | 1 | 1 | 3.3595 | Jan | 1 | 1 | 3.0208 | 3.3595 | 3.1684 | 10.69% | 3.202 | Dec | 31 | 24 | ○ | 1 | 1
620 East & West Windows | 3.145 | Dec | 31 | 24 | 3.0379 | Jan | 1 | 1 | 3.068 | Jan | 1 | 0 | 3.2291 | Dec | 31 | 24 | 3.253 | Jan | 1 | 1 | 3.3846 | Jan | 1 | 1 | 3.0379 | 3.3846 | 3.1863 | 10.88% | 3.248 | Dec | 31 | 24 | ○ | 2 | 2
630 E&W Windows + Overhang & Fins | 3.252 | Dec | 31 | 24 | 3.0394 | Jan | 1 | 1 | 3.072 | Jan | 1 | 0 | 3.2066 | Dec | 31 | 24 | 3.259 | Jan | 1 | 1 | 3.3876 | Jan | 1 | 1 | 3.0394 | 3.3876 | 3.2027 | 10.87% | 3.254 | Dec | 31 | 24 | ○ | 3 | 3
640 Case 600 with Htg. Temp. Setback | 4.633 | Feb | 8 | 9 | 4.2225 | Nov | 26 | 8 | 4.658 | Nov | 26 | 7 | 4.5585 | Nov | 26 | 8 | 4.101 | Nov | 26 | 8 | 4.0385 | Nov | 26 | 8 | 4.0385 | 4.658 | 4.3686 | 14.18% | 4.3 | Feb | 8 | 9 | ○ | 4 | 4
650 Case 600 with Night Ventilation | 0 |  |  |  | 0 | Jan | 1 | 1 | 0 |  |  |  | 0 | Jan | 1 | 1 | 0 | Jan | 1 | 1 | 0 | Dec | 31 | 0 | 0 | 0 | 0 | ---- | 0 |  |  |  | ○ | 5 | 5
660 Low-E Windows | 2.62 | Nov | 26 | 8 | 2.7583 | Jan | 1 | 1 | 2.798 | Jan | 1 | 0 | 2.8311 | Dec | 31 | 24 | 2.846 | Jan | 1 | 1 | 2.9552 | Jan | 1 | 1 | 2.62 | 2.9552 | 2.8014 | 11.96% | 2.863 | Dec | 31 | 24 | ○ |  | 6
670 Single-Pane Windows | 4.122 | Nov | 26 | 8 | 3.6554 | Jan | 1 | 1 | 3.812 | Jan | 1 | 0 | 3.8535 | Nov | 26 | 7 | 3.992 | Nov | 26 | 7 | 4.221 | Nov | 26 | 8 | 3.6554 | 4.221 | 3.9427 | 14.34% | 3.878 | Nov | 26 | 7 | ○ |  | 7
680 Case 600 with Increased Insulation | 2.126 | Nov | 26 | 8 | 1.7776 | Feb | 9 | 6 | 1.811 | Jan | 1 | 1 | 2.0524 | Nov | 26 | 7 | 2.022 | Feb | 9 | 7 | 2.1147 | Nov | 26 | 8 | 1.7776 | 2.126 | 1.984 | 17.56% | 2.087 | Nov | 26 | 7 | ○ |  | 8
685 Case 600 with "20/20" Thermostat | 3.169 | Nov | 26 | 8 | 3.0319 | Jan | 1 | 1 | 3.054 | Jan | 1 | 0 | 3.2232 | Dec | 31 | 24 | 3.247 | Jan | 1 | 1 | 3.3744 | Jan | 1 | 1 | 3.0319 | 3.3744 | 3.1832 | 10.76% | 3.226 | Dec | 31 | 24 | ○ |  | 9
695 Case 685 with Increased Insulation | 2.138 | Nov | 26 | 8 | 1.7953 | Jan | 1 | 1 | 1.855 | Jan | 1 | 1 | 2.0718 | Dec | 31 | 24 | 2.025 | Nov | 26 | 7 | 2.1177 | Nov | 26 | 8 | 1.7953 | 2.138 | 2.0005 | 17.13% | 2.093 | Nov | 26 | 7 | ○ |  | 10
900 South Windows | 2.551 | Feb | 8 | 24 | 2.4434 | Feb | 9 | 6 | 2.453 | Feb | 9 | 5 | 2.6875 | Feb | 9 | 6 | 2.633 | Feb | 9 | 7 | 2.7785 | Feb | 9 | 7 | 2.4434 | 2.7785 | 2.5911 | 12.93% | 2.672 | Feb | 9 | 6 | ○ | 6 | 11
910 S. Windows + Overhang | 2.761 | Feb | 8 | 24 | 2.469 | Feb | 9 | 6 | 2.474 | Feb | 9 | 5 | 2.6989 | Feb | 9 | 6 | 2.684 | Feb | 9 | 7 | 2.7992 | Feb | 9 | 6 | 2.469 | 2.7992 | 2.6477 | 12.47% | 2.692 | Feb | 9 | 6 | ○ | 7 | 12
920 East & West Windows | 2.895 | Nov | 26 | 8 | 2.5124 | Feb | 9 | 6 | 2.513 | Feb | 9 | 5 | 2.7702 | Feb | 9 | 6 | 2.706 | Feb | 9 | 7 | 2.8643 | Feb | 9 | 6 | 2.5124 | 2.895 | 2.7101 | 14.12% | 2.748 | Feb | 9 | 6 | ○ | 8 | 13
930 E&W Windows + Overhang & Fins | 2.968 | Dec | 31 | 24 | 2.537 | Feb | 9 | 6 | 2.549 | Feb | 9 | 5 | 2.7849 | Feb | 9 | 6 | 2.765 | Feb | 9 | 6 | 2.9004 | Feb | 9 | 6 | 2.537 | 2.968 | 2.7507 | 15.67% | 2.781 | Feb | 9 | 6 | ○ | 9 | 14
940 Case 900 with Htg. Temp. Setback | 3.882 | Feb | 8 | 9 | 3.0519 | Jan | 1 | 9 | 3.659 | Feb | 9 | 7 | 3.1428 | Dec | 31 | 9 | 3.122 | Feb | 9 | 9 | 3.4048 | Jan | 1 | 9 | 3.0519 | 3.882 | 3.3771 | 24.58% | 3.479 | Dec | 31 | 9 | ○ | 10 | 15
950 Case 900 with Night Ventilation | 0 |  |  |  | 0 | Jan | 1 | 1 | 0 |  |  |  | 0 | Jan | 1 | 1 | 0 | Jan | 1 | 1 | 0 | Dec | 31 | 0 | 0 | 0 | 0 | ---- | 0 |  |  |  | ○ | 11 | 16
960 Sunspace |  |  |  |  | 2.132 | Feb | 9 | 6 | 2.085 | Jan | 1 | 0 | 2.2594 | Feb | 9 | 6 | 2.201 | Feb | 9 | 6 | 2.3004 | Feb | 9 | 6 | 2.085 | 2.3004 | 2.1956 | 9.811% | 2.298 | Feb | 9 | 6 | ○ | 12 | 17
980 Case 900 with Increased Insulation | 1.693 | Feb | 8 | 24 | 1.2538 | Feb | 9 | 6 | 1.382 | Feb | 9 | 5 | 1.5378 | Feb | 9 | 6 | 1.473 | Feb | 9 | 7 | 1.5921 | Feb | 9 | 7 | 1.2538 | 1.693 | 1.4886 | 29.5% | 1.646 | Feb | 9 | 6 | ○ |  | 18
985 Case 900 with "20/20" Thermostat | 2.754 | Feb | 8 | 24 | 2.4522 | Feb | 9 | 6 | 2.458 | Feb | 9 | 5 | 2.6954 | Feb | 9 | 6 | 2.642 | Feb | 9 | 7 | 2.7854 | Feb | 9 | 6 | 2.4522 | 2.7854 | 2.6312 | 12.67% | 2.678 | Feb | 9 | 6 | ○ |  | 19
995 Case 985 with Increased Insulation | 1.711 | Nov | 26 | 8 | 1.3696 | Feb | 9 | 6 | 1.462 | Feb | 9 | 5 | 1.6221 | Feb | 9 | 6 | 1.56 | Feb | 9 | 7 | 1.662 | Feb | 9 | 6 | 1.3696 | 1.711 | 1.5644 | 21.83% | 1.697 | Feb | 9 | 6 | ○ |  | 20
195 Solid Conduction | 1.802 | Dec | 31 | 24 | 1.7907 | Jan | 1 | 1 | 1.799 | Jan | 1 | 0 | 1.7944 | Dec | 31 | 24 | 1.802 | Jan | 1 | 1 | 1.7959 | Jan | 1 | 1 | 1.7907 | 1.802 | 1.7973 | 0.6288% | 1.733 | Dec | 31 | 24 | -510.6% | 13 | 21
200 Surface Convection (Int & Ext IR="off") | 2.272 | Nov | 26 | 8 | 2.226 | Nov | 26 | 8 | 2.308 | Jan | 1 | 0 | 2.3413 | Nov | 26 | 8 | 2.275 | Dec | 31 | 24 | 2.3527 | Nov | 26 | 8 | 2.226 | 2.3527 | 2.2958 | 5.518% | 2.185 | Nov | 26 | 7 | -32.39% | 14 | 22
210 Infrared Radiation (Int IR="off", Ext IR="on") | 2.374 | Dec | 31 | 24 | 2.629 | Jan | 1 | 2 | 2.605 | Jan | 1 | 0 | 2.5646 | Dec | 31 | 24 | 2.671 | Jan | 1 | 1 | 2.7498 | Jan | 1 | 1 | 2.374 | 2.7498 | 2.5989 | 14.46% | 2.504 | Dec | 31 | 24 | ○ | 15 | 23
215 Infrared Radiation (Int IR="on", Ext IR="off") | 2.521 | Nov | 26 | 8 | 2.42 | Nov | 26 | 8 | 2.52 | Jan | 1 | 0 | 2.4778 | Nov | 26 | 8 | 2.39 | Nov | 26 | 8 | 2.4894 | Nov | 26 | 8 | 2.39 | 2.521 | 2.4697 | 5.304% | 2.407 | Nov | 26 | 7 | ○ | 16 | 24
220 In-Depth Base Case | 2.631 | Nov | 26 | 8 | 2.8394 | Jan | 1 | 1 | 2.863 | Jan | 1 | 0 | 2.692 | Dec | 31 | 24 | 2.788 | Jan | 1 | 1 | 2.8786 | Jan | 1 | 1 | 2.631 | 2.8786 | 2.782 | 8.899% | 2.734 | Dec | 31 | 24 | ○ | 17 | 25
230 Infiltration | 4.219 | Dec | 31 | 24 | 4.1329 | Jan | 1 | 1 | 4.223 | Jan | 1 | 0 | 4.3161 | Dec | 31 | 24 | 4.16 | Jan | 1 | 1 | 4.3153 | Jan | 1 | 1 | 4.1329 | 4.3161 | 4.2277 | 4.333% | 4.207 | Dec | 31 | 24 | ○ | 18 | 26
240 Internal Gains | 2.431 | Nov | 26 | 8 | 2.6514 | Jan | 1 | 1 | 2.685 | Jan | 1 | 0 | 2.5071 | Dec | 31 | 24 | 2.605 | Jan | 1 | 1 | 2.6931 | Jan | 1 | 1 | 2.431 | 2.6931 | 2.5954 | 10.1% | 2.556 | Dec | 31 | 24 | ○ | 19 | 27
250 Exterior Shortwave Absorptance | 2.631 | Nov | 26 | 8 | 2.8371 | Jan | 1 | 1 | 2.855 | Jan | 1 | 0 | 2.6874 | Dec | 31 | 24 | 2.78 | Jan | 1 | 1 | 2.8744 | Jan | 1 | 1 | 2.631 | 2.8744 | 2.7775 | 8.762% | 2.719 | Dec | 31 | 24 | ○ | 20 | 28
270 South Solar Windows |  |  |  |  | 2.6114 | Jan | 1 | 2 | 2.56 | Jan | 1 | 1 | 2.5966 | Dec | 31 | 24 | 2.748 | Jan | 1 | 1 | 2.8432 | Jan | 1 | 2 | 2.56 | 2.8432 | 2.6718 | 10.6% | 2.668 | Dec | 31 | 24 | ○ | 21 | 29
280 Cavity Albedo |  |  |  |  | 2.6122 | Jan | 1 | 2 | 2.568 | Jan | 1 | 1 | 2.602 | Dec | 31 | 24 | 2.752 | Jan | 1 | 1 | 2.8487 | Jan | 1 | 1 | 2.568 | 2.8487 | 2.6766 | 10.49% | 2.687 | Dec | 31 | 24 | ○ | 22 | 30
290 South Shading |  |  |  |  | 2.6115 | Jan | 1 | 2 | 2.561 | Jan | 1 | 1 | 2.5834 | Dec | 31 | 24 | 2.75 | Jan | 1 | 1 | 2.8434 | Jan | 1 | 2 | 2.561 | 2.8434 | 2.6699 | 10.58% | 2.67 | Dec | 31 | 24 | ○ | 23 | 31
300 East/West Window |  |  |  |  | 2.6141 | Jan | 1 | 1 | 2.589 | Jan | 1 | 0 | 2.6031 | Dec | 31 | 24 | 2.766 | Jan | 1 | 1 | 2.8536 | Jan | 1 | 1 | 2.589 | 2.8536 | 2.6852 | 9.856% | 2.693 | Dec | 31 | 24 | ○ | 24 | 32
310 East/West Shading |  |  |  |  | 2.6149 | Jan | 1 | 1 | 2.592 | Jan | 1 | 0 | 2.5801 | Dec | 31 | 24 | 2.771 | Jan | 1 | 1 | 2.8563 | Jan | 1 | 1 | 2.5801 | 2.8563 | 2.6829 | 10.3% | 2.7 | Dec | 31 | 24 | ○ | 25 | 33
320 Thermostat |  |  |  |  | 2.609 | Jan | 1 | 1 | 2.546 | Jan | 1 | 1 | 2.5735 | Dec | 31 | 24 | 2.733 | Jan | 1 | 2 | 2.8335 | Jan | 1 | 2 | 2.546 | 2.8335 | 2.659 | 10.81% | 2.642 | Feb | 9 | 6 | ○ | 26 | 34
395 Low Mass Solid Conduction | 1.948 | Dec | 31 | 24 | 2.1574 | Jan | 1 | 2 | 2.085 | Jan | 1 | 1 | 1.9517 | Dec | 31 | 24 | 2.09 | Jan | 1 | 2 | 2.1613 | Jan | 1 | 2 | 1.948 | 2.1613 | 2.0656 | 10.33% | 2.04 | Dec | 31 | 24 | ○ | 27 | 35
400 Low Mass High Cond. Wall Elements | 2.559 | Nov | 26 | 8 | 2.8394 | Jan | 1 | 1 | 2.863 | Jan | 1 | 0 | 2.692 | Dec | 31 | 24 | 2.788 | Jan | 1 | 1 | 2.8786 | Jan | 1 | 1 | 2.559 | 2.8786 | 2.77 | 11.54% | 2.734 | Dec | 31 | 24 | ○ | 28 | 36
410 Low Mass Infiltration | 3.338 | Dec | 31 | 24 | 3.4407 | Jan | 1 | 1 | 3.543 | Jan | 1 | 0 | 3.504 | Dec | 31 | 24 | 3.473 | Jan | 1 | 1 | 3.5969 | Jan | 1 | 1 | 3.338 | 3.5969 | 3.4826 | 7.435% | 3.47 | Dec | 31 | 24 | ○ | 29 | 37
420 Low Mass Internal Gains | 3.138 | Dec | 31 | 24 | 3.2562 | Jan | 1 | 1 | 3.365 | Jan | 1 | 0 | 3.3191 | Dec | 31 | 24 | 3.29 | Jan | 1 | 1 | 3.4115 | Jan | 1 | 1 | 3.138 | 3.4115 | 3.2966 | 8.295% | 3.292 | Dec | 31 | 24 | ○ | 30 | 38
430 Low Mass Ext. Shortwave Absorptance | 3.3 | Dec | 31 | 24 | 3.2539 | Jan | 1 | 1 | 3.36 | Jan | 1 | 0 | 3.3163 | Dec | 31 | 24 | 3.285 | Jan | 1 | 1 | 3.4088 | Jan | 1 | 1 | 3.2539 | 3.4088 | 3.3207 | 4.666% | 3.283 | Dec | 31 | 24 | ○ | 31 | 39
440 Low Mass Cavity Albedo |  |  |  |  | 3.0272 | Jan | 1 | 1 | 3.06 | Jan | 1 | 0 | 3.2187 | Dec | 31 | 24 | 3.237 | Jan | 1 | 1 | 3.3743 | Jan | 1 | 1 | 3.0272 | 3.3743 | 3.1834 | 10.9% | 3.227 | Dec | 31 | 24 | ○ | 32 | 40
450 Constant Interior and Exterior Surf Coeffs | 2.989 | Nov | 26 | 8 | 2.9783 | Jan | 1 | 1 | 2.753 | Jan | 1 | 0 | 3.0998 | Dec | 31 | 24 | 3.042 | Jan | 1 | 1 | 3.0373 | Jan | 1 | 1 | 2.753 | 3.0998 | 2.9832 | 11.63% | 3.036 | Dec | 31 | 24 | ○ |  | 41
460 Constant Interior Surface Coefficients | 3.055 | Nov | 26 | 8 | 2.9714 | Jan | 1 | 1 | 2.98 | Jan | 1 | 0 | 3.0911 | Dec | 31 | 24 | 3.101 | Jan | 1 | 1 | 3.1597 | Jan | 1 | 1 | 2.9714 | 3.1597 | 3.0597 | 6.155% | 3.116 | Dec | 31 | 24 | ○ |  | 42
470 Constant Exterior Surface Coefficients | 3.118 | Nov | 26 | 8 | 3.0007 | Jan | 1 | 1 | 2.807 | Jan | 1 | 0 | 3.2067 | Dec | 31 | 24 | 3.169 | Jan | 1 | 1 | 3.2315 | Jan | 1 | 1 | 2.807 | 3.2315 | 3.0888 | 13.74% | 3.112 | Dec | 31 | 24 | ○ |  | 43
800 High Mass High Cond. Wall Elements | 2.957 | Dec | 31 | 24 | 2.7776 | Feb | 9 | 6 | 2.864 | Feb | 9 | 5 | 2.9237 | Feb | 9 | 6 | 2.84 | Feb | 9 | 7 | 2.9669 | Feb | 9 | 6 | 2.7776 | 2.9669 | 2.8882 | 6.555% | 2.846 | Feb | 9 | 6 | ○ | 33 | 44
810 High Mass Cavity Albedo |  |  |  |  | 2.5001 | Feb | 9 | 6 | 2.512 | Feb | 9 | 5 | 2.749 | Feb | 9 | 6 | 2.695 | Feb | 9 | 7 | 2.8447 | Feb | 9 | 6 | 2.5001 | 2.8447 | 2.6602 | 12.95% | 2.727 | Feb | 9 | 6 | ○ | 34 | 45
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-4. Annual Hourly Integrated Peak Sensible Cooling Loads
Case: Simulation Model:; kW: BSIMAC; kW: CSE; kW: DeST; kW: EnergyPlus; kW: ESP-r; kW: TRNSYS; Min kW: Example Result Statistics |  |  | Tested Prg
Min kW: Min; Max kW: Max; Mean kW: Mean | (Max-Min)/
Case | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | kW | kW | Mean** (%) | kW | Mo. | Day | Hr
600 Base Case, South Windows | 5.65 | Jan | 22 | 15 | 6.481 | Jan | 22 | 14 | 5.422 | Jan | 22 | 14 | 6.3516 | Jan | 22 | 14 | 6.193 | Jan | 22 | 14 | 6.0457 | Jan | 22 | 14 | 5.422 | 6.481 | 6.0239 | 17.58% | 5.609 | Oct | 18 | 14 | ○
610 S. Windows + Overhang | 5.466 | Jan | 22 | 15 | 6.4322 | Dec | 1 | 14 | 5.331 | Jan | 22 | 14 | 6.1345 | Dec | 1 | 14 | 5.934 | Jan | 22 | 14 | 5.8678 | Dec | 1 | 14 | 5.331 | 6.4322 | 5.8609 | 18.79% | 5.344 | Dec | 1 | 14 | ○
620 East & West Windows | 4.704 | Jun | 26 | 18 | 4.4928 | Jun | 26 | 17 | 3.955 | Jun | 26 | 17 | 4.7974 | Jun | 26 | 17 | 4.622 | Jun | 26 | 17 | 4.5883 | Jun | 26 | 17 | 3.955 | 4.7974 | 4.5266 | 18.61% | 4.236 | Jun | 26 | 17 | ○
630 E&W Windows + Overhang & Fins | 4.121 | Jun | 26 | 18 | 3.9983 | Jun | 26 | 18 | 3.526 | Jun | 26 | 17 | 4.2122 | Jun | 26 | 17 | 3.971 | Jun | 26 | 17 | 3.9494 | Jun | 26 | 17 | 3.526 | 4.2122 | 3.963 | 17.31% | 3.631 | Jun | 26 | 17 | ○
640 Case 600 with Htg. Temp. Setback | 5.65 | Jan | 22 | 15 | 6.429 | Jan | 22 | 14 | 5.365 | Jan | 22 | 14 | 6.2974 | Jan | 22 | 14 | 6.127 | Jan | 22 | 14 | 5.9671 | Jan | 22 | 14 | 5.365 | 6.429 | 5.9726 | 17.81% | 5.495 | Oct | 18 | 14 | ○
650 Case 600 with Night Ventilation | 5.648 | Jan | 22 | 15 | 6.2897 | Dec | 1 | 14 | 5.045 | Oct | 18 | 14 | 6.1381 | Oct | 18 | 14 | 5.961 | Oct | 18 | 14 | 5.7975 | Oct | 18 | 14 | 5.045 | 6.2897 | 5.8132 | 21.41% | 5.441 | Oct | 18 | 14 | ○
660 Low-E Windows | 3.343 | Oct | 18 | 15 | 3.933 | Oct | 1 | 13 | 3.355 | Oct | 11 | 14 | 3.7703 | Oct | 18 | 14 | 3.53 | Oct | 1 | 14 | 3.4574 | Oct | 18 | 14 | 3.343 | 3.933 | 3.5648 | 16.55% | 3.435 | Oct | 18 | 14 | ○
670 Single-Pane Windows | 6.217 | Oct | 18 | 14 | 6.9253 | Oct | 1 | 13 | 5.839 | Oct | 10 | 13 | 6.8062 | Jan | 22 | 14 | 6.482 | Oct | 18 | 14 | 6.4013 | Oct | 18 | 14 | 5.839 | 6.9253 | 6.4451 | 16.85% | 5.941 | Oct | 18 | 14 | ○
680 Case 600 with Increased Insulation | 5.761 | Jan | 22 | 15 | 7.0513 | Jan | 22 | 14 | 5.861 | Jan | 22 | 14 | 6.7702 | Jan | 22 | 14 | 6.676 | Jan | 22 | 14 | 6.5566 | Jan | 22 | 14 | 5.761 | 7.0513 | 6.446 | 20.02% | 6.028 | Jan | 22 | 14 | ○
685 Case 600 with "20/20" Thermostat | 6.318 | Jan | 22 | 15 | 7.1594 | Jan | 22 | 14 | 6.071 | Jan | 22 | 14 | 7.1068 | Jan | 22 | 14 | 6.934 | Jan | 22 | 14 | 6.8674 | Jan | 22 | 14 | 6.071 | 7.1594 | 6.7428 | 16.14% | 6.288 | Oct | 18 | 14 | ○
695 Case 685 with Increased Insulation | 6.232 | Jan | 22 | 15 | 7.5407 | Jan | 22 | 14 | 6.355 | Jan | 22 | 14 | 7.3343 | Jan | 22 | 14 | 7.239 | Jan | 22 | 14 | 7.1752 | Jan | 22 | 14 | 6.232 | 7.5407 | 6.9794 | 18.75% | 6.618 | Jan | 22 | 14 | ○
900 South Windows | 3.039 | Oct | 1 | 15 | 3.3764 | Oct | 1 | 14 | 2.556 | Sep | 11 | 14 | 3.0404 | Oct | 1 | 14 | 2.896 | Oct | 12 | 15 | 2.9401 | Oct | 1 | 14 | 2.556 | 3.3764 | 2.9747 | 27.58% | 2.818 | Sep | 11 | 14 | ○
910 S. Windows + Overhang | 2.493 | Oct | 18 | 14 | 2.7221 | Oct | 2 | 15 | 2.103 | Oct | 12 | 14 | 2.2221 | Oct | 18 | 15 | 2.212 | Oct | 2 | 15 | 2.081 | Oct | 12 | 15 | 2.081 | 2.7221 | 2.3055 | 27.8% | 2.136 | Oct | 12 | 15 | ○
920 East & West Windows | 3.481 | Jun | 26 | 18 | 3.0567 | Jun | 26 | 18 | 2.71 | Jun | 26 | 17 | 3.2603 | Jun | 26 | 18 | 3.099 | Jun | 26 | 18 | 3.1541 | Jun | 26 | 18 | 2.71 | 3.481 | 3.1269 | 24.66% | 2.909 | Jun | 26 | 17 | ○
930 E&W Windows + Overhang & Fins | 3.052 | Jun | 26 | 18 | 2.6618 | Jun | 26 | 18 | 2.335 | Jun | 26 | 17 | 2.7815 | Jun | 26 | 18 | 2.494 | Jun | 26 | 18 | 2.6131 | Jun | 26 | 18 | 2.335 | 3.052 | 2.6562 | 26.99% | 2.436 | Jun | 26 | 18 | ○
940 Case 900 with Htg. Temp. Setback | 3.158 | Oct | 1 | 15 | 3.3764 | Oct | 1 | 14 | 2.556 | Sep | 11 | 14 | 3.04 | Oct | 1 | 14 | 2.891 | Oct | 12 | 15 | 2.9376 | Oct | 1 | 14 | 2.556 | 3.3764 | 2.9932 | 27.41% | 2.818 | Sep | 11 | 14 | ○
950 Case 900 with Night Ventilation | 2.366 | Sep | 10 | 15 | 2.3635 | Sep | 4 | 15 | 2.054 | Sep | 11 | 14 | 2.3875 | Sep | 11 | 15 | 2.202 | Sep | 10 | 15 | 2.2364 | Sep | 11 | 15 | 2.054 | 2.3875 | 2.2682 | 14.7% | 2.337 | Sep | 11 | 15 | ○
960 Sunspace |  |  |  |  | 1.3771 | Jun | 26 | 17 | 1.367 | Jun | 26 | 16 | 1.4799 | Jun | 26 | 17 | 1.403 | Jun | 26 | 17 | 1.3385 | Jun | 26 | 17 | 1.3385 | 1.4799 | 1.3931 | 10.15% | 1.358 | Jun | 26 | 16 | ○
980 Case 900 with Increased Insulation | 3.384 | Oct | 18 | 14 | 3.668 | Oct | 2 | 14 | 2.93 | Oct | 18 | 14 | 3.4501 | Oct | 18 | 15 | 3.341 | Oct | 12 | 15 | 3.3126 | Oct | 12 | 14 | 2.93 | 3.668 | 3.3476 | 22.05% | 3.157 | Oct | 18 | 14 | ○
985 Case 900 with "20/20" Thermostat | 3.977 | Oct | 18 | 14 | 4.2253 | Oct | 1 | 14 | 3.208 | Oct | 11 | 14 | 3.9148 | Oct | 18 | 15 | 3.736 | Oct | 12 | 15 | 3.8847 | Oct | 1 | 14 | 3.208 | 4.2253 | 3.8243 | 26.6% | 3.516 | Oct | 1 | 14 | ○
995 Case 985 with Increased Insulation | 4.129 | Jan | 22 | 14 | 4.2238 | Jan | 22 | 15 | 3.315 | Jan | 22 | 14 | 4.1774 | Jan | 22 | 15 | 3.954 | Jan | 22 | 15 | 4.1149 | Jan | 22 | 15 | 3.315 | 4.2238 | 3.9857 | 22.8% | 3.643 | Jan | 22 | 15 | ○
195 Solid Conduction | 1.118 | Jun | 26 | 17 | 0.99425 | Jun | 26 | 17 | 0.973 | Jun | 26 | 16 | 1.041 | Jun | 26 | 17 | 0.944 | Jun | 26 | 17 | 0.99351 | Jun | 26 | 17 | 0.944 | 1.118 | 1.0106 | 17.22% | 0.977 | Jun | 26 | 17 | ○
200 Surface Convection (Int & Ext IR="off") | 1.271 | Jun | 26 | 17 | 1.2152 | Jun | 26 | 17 | 1.239 | Jun | 26 | 16 | 1.3075 | Jun | 26 | 17 | 1.198 | Jun | 26 | 17 | 1.2589 | Jun | 26 | 17 | 1.198 | 1.3075 | 1.2483 | 8.77% | 1.222 | Jun | 26 | 17 | ○
210 Infrared Radiation (Int IR="off", Ext IR="on") | 1.193 | Jun | 26 | 17 | 0.94562 | Jun | 13 | 15 | 0.937 | Jun | 26 | 16 | 1.0844 | Jun | 26 | 17 | 0.877 | Jun | 14 | 14 | 0.88416 | Jun | 26 | 18 | 0.877 | 1.193 | 0.98686 | 32.02% | 0.909 | Jun | 26 | 18 | ○
215 Infrared Radiation (Int IR="on", Ext IR="off") | 1.393 | Jun | 26 | 17 | 1.3692 | Jun | 26 | 17 | 1.386 | Jun | 26 | 16 | 1.4004 | Jun | 26 | 17 | 1.366 | Jun | 26 | 17 | 1.3521 | Jun | 26 | 17 | 1.3521 | 1.4004 | 1.3778 | 3.505% | 1.345 | Jun | 26 | 17 | -14.71%
220 In-Depth Base Case | 1.336 | Jun | 26 | 18 | 1.1085 | Jun | 13 | 15 | 1.04 | Jun | 26 | 16 | 1.1845 | Jun | 26 | 18 | 1.012 | Jun | 14 | 15 | 0.96801 | Jun | 26 | 18 | 0.96801 | 1.336 | 1.1082 | 33.21% | 1.018 | Jun | 26 | 18 | ○
230 Infiltration | 1.994 | Jun | 26 | 17 | 1.7281 | Jun | 26 | 17 | 1.734 | Jun | 26 | 16 | 1.8409 | Jun | 26 | 17 | 1.701 | Jun | 26 | 17 | 1.6936 | Jun | 26 | 17 | 1.6936 | 1.994 | 1.7819 | 16.86% | 1.732 | Jun | 26 | 17 | ○
240 Internal Gains | 1.534 | Jun | 26 | 18 | 1.2947 | Jun | 13 | 15 | 1.218 | Jun | 26 | 16 | 1.3659 | Jun | 26 | 18 | 1.192 | Jun | 14 | 15 | 1.1496 | Jun | 26 | 18 | 1.1496 | 1.534 | 1.2924 | 29.75% | 1.195 | Jun | 26 | 18 | ○
250 Exterior Shortwave Absorptance | 2.913 | Sep | 12 | 14 | 2.79 | Sep | 12 | 14 | 2.751 | Sep | 3 | 14 | 2.8666 | Sep | 12 | 14 | 3.034 | Sept | 12 | 14 | 2.688 | Sep | 12 | 14 | 2.688 | 3.034 | 2.8404 | 12.18% | 2.735 | Sep | 12 | 14 | ○
270 South Solar Windows |  |  |  |  | 7.011 | Jan | 22 | 14 | 5.832 | Jan | 22 | 14 | 6.8388 | Jan | 22 | 14 | 6.613 | Jan | 22 | 14 | 6.6375 | Jan | 22 | 14 | 5.832 | 7.011 | 6.5865 | 17.9% | 6.04 | Jan | 22 | 14 | ○
280 Cavity Albedo |  |  |  |  | 4.7651 | Jan | 22 | 14 | 3.768 | Dec | 1 | 13 | 4.7272 | Jan | 22 | 14 | 4.676 | Jan | 22 | 14 | 4.3999 | Jan | 22 | 14 | 3.768 | 4.7651 | 4.4672 | 22.32% | 4.165 | Jan | 22 | 14 | ○
290 South Shading |  |  |  |  | 6.8722 | Jan | 22 | 14 | 5.739 | Jan | 22 | 14 | 6.5946 | Jan | 22 | 14 | 6.411 | Jan | 22 | 14 | 6.4019 | Jan | 22 | 14 | 5.739 | 6.8722 | 6.4037 | 17.7% | 5.791 | Jan | 22 | 14 | ○
300 East/West Window |  |  |  |  | 4.1631 | Jun | 26 | 17 | 3.695 | Jun | 26 | 17 | 4.4755 | Jun | 26 | 17 | 4.221 | Jun | 26 | 17 | 4.2782 | Jun | 26 | 17 | 3.695 | 4.4755 | 4.1666 | 18.73% | 3.924 | Jun | 26 | 17 | ○
310 East/West Shading |  |  |  |  | 3.7959 | Jun | 26 | 18 | 3.252 | Jun | 26 | 17 | 3.9695 | Jun | 26 | 18 | 3.618 | Jun | 26 | 18 | 3.7015 | Jun | 26 | 18 | 3.252 | 3.9695 | 3.6674 | 19.57% | 3.376 | Jun | 26 | 18 | ○
320 Thermostat |  |  |  |  | 6.4733 | Jan | 22 | 14 | 5.304 | Jan | 22 | 14 | 6.2091 | Jan | 22 | 14 | 5.993 | Jan | 22 | 14 | 5.9494 | Jan | 22 | 14 | 5.304 | 6.4733 | 5.9858 | 19.53% | 5.436 | Jan | 22 | 14 | ○
395 Low Mass Solid Conduction | 0.547 | Jun | 26 | 18 | 0.3575 | Jun | 14 | 18 | 0.308 | Jun | 14 | 16 | 0.37747 | Jun | 26 | 19 | 0.294 | Aug | 5 | 18 | 0.2652 | Jun | 14 | 18 | 0.2652 | 0.547 | 0.3582 | 78.67% | 0.282 | Jun | 14 | 17 | ○
400 Low Mass High Cond. Wall Elements | 0.798 | Jun | 26 | 18 | 0.49365 | Jun | 14 | 15 | 0.457 | Jun | 26 | 17 | 0.60691 | Jun | 26 | 18 | 0.456 | Aug | 5 | 17 | 0.37199 | Jun | 14 | 17 | 0.37199 | 0.798 | 0.53059 | 80.29% | 0.445 | Jun | 26 | 18 | ○
410 Low Mass Infiltration | 1.011 | Jun | 26 | 17 | 0.69988 | Jun | 26 | 18 | 0.709 | Jun | 26 | 16 | 0.82785 | Jun | 26 | 18 | 0.624 | Jun | 26 | 18 | 0.60368 | Jun | 26 | 18 | 0.60368 | 1.011 | 0.7459 | 54.61% | 0.691 | Jun | 26 | 18 | ○
420 Low Mass Internal Gains | 1.208 | Jun | 26 | 17 | 0.90853 | Jun | 26 | 18 | 0.917 | Jun | 26 | 16 | 1.0325 | Jun | 26 | 18 | 0.836 | Jun | 26 | 17 | 0.81407 | Jun | 26 | 18 | 0.81407 | 1.208 | 0.95269 | 41.35% | 0.886 | Jun | 26 | 18 | ○
430 Low Mass Ext. Shortwave Absorptance | 2.167 | Jun | 26 | 16 | 1.8398 | Jun | 26 | 15 | 1.84 | Jun | 26 | 15 | 1.9294 | Jun | 26 | 16 | 1.874 | Jul | 17 | 14 | 1.7041 | Jun | 26 | 15 | 1.7041 | 2.167 | 1.8924 | 24.46% | 1.677 | Jun | 26 | 16 | -5.85%
440 Low Mass Cavity Albedo |  |  |  |  | 4.6655 | Oct | 1 | 13 | 3.766 | Oct | 11 | 13 | 4.686 | Oct | 18 | 14 | 4.679 | Oct | 18 | 14 | 4.3076 | Oct | 18 | 14 | 3.766 | 4.686 | 4.4208 | 20.81% | 4.184 | Oct | 18 | 14 | ○
450 Constant Interior and Exterior Surf Coeffs | 5.812 | Jan | 22 | 15 | 6.1798 | Jan | 22 | 14 | 6.063 | Jan | 22 | 13 | 6.4663 | Jan | 22 | 14 | 6.501 | Jan | 22 | 14 | 6.3134 | Jan | 22 | 14 | 5.812 | 6.501 | 6.2226 | 11.07% | 6.399 | Jan | 22 | 14 | ○
460 Constant Interior Surface Coefficients | 5.804 | Jan | 22 | 15 | 6.2429 | Jan | 22 | 14 | 5.902 | Jan | 22 | 13 | 6.3742 | Jan | 22 | 14 | 6.304 | Jan | 22 | 14 | 6.0689 | Jan | 22 | 14 | 5.804 | 6.3742 | 6.116 | 9.323% | 6.152 | Jan | 22 | 14 | ○
470 Constant Exterior Surface Coefficients | 5.695 | Jan | 22 | 15 | 6.3877 | Jan | 22 | 14 | 5.57 | Jan | 22 | 14 | 6.4436 | Jan | 22 | 14 | 6.407 | Jan | 22 | 14 | 6.32 | Jan | 22 | 14 | 5.57 | 6.4436 | 6.1372 | 14.24% | 5.768 | Jan | 22 | 14 | ○
800 High Mass High Cond. Wall Elements | 1.286 | Jun | 26 | 16 | 1.1019 | Aug | 5 | 15 | 1.157 | Aug | 5 | 14 | 1.0458 | Jun | 26 | 16 | 1.052 | Aug | 5 | 15 | 0.93559 | Aug | 5 | 15 | 0.93559 | 1.286 | 1.0964 | 31.96% | 1.016 | Aug | 5 | 15 | ○
810 High Mass Cavity Albedo |  |  |  |  | 2.4105 | Sep | 4 | 15 | 1.94 | Sep | 11 | 14 | 2.2702 | Sep | 11 | 15 | 2.179 | Sep | 4 | 15 | 2.1129 | Sep | 11 | 15 | 1.94 | 2.4105 | 2.1825 | 21.56% | 2.233 | Sep | 11 | 14 | ○
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-5. Free-Float Temperature Output
MAXIMUM ANNUAL HOURLY INTEGRATED ZONE TEMPERATURE
Case: Simulation Model:; kW: BSIMAC; kW: CSE; kW: DeST; kW: EnergyPlus; kW: ESP-r; kW: TRNSYS; Min kW: Example Result Statistics |  |  | Tested Prg
Min kW: Min; Max kW: Max; Mean kW: Mean | (Max-Min)/
Case | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | T (°C) | T (°C) | Mean** (%) | T (°C) | Mo. | Day | Hr
600FF - Low Mass with S. Windows | 63.4 | Oct | 18 | 17 | 68.3608 | Oct | 1 | 16 | 65 | Oct | 11 | 15 | 63.8408 | Oct | 18 | 16 | 64.6 | Oct | 1 | 16 | 62.3692 | Oct | 1 | 15 | 62.3692 | 68.3608 | 64.5951 | 9.276% | 64.46 | Oct | 18 | 15 | ○
900FF - High Mass with S. Windows | 46 | Oct | 1 | 17 | 45.1138 | Sep | 4 | 15 | 44.46 | Sep | 11 | 15 | 44.2922 | Sep | 12 | 15 | 44.3 | Sep | 12 | 16 | 43.2522 | Sep | 12 | 15 | 43.2522 | 46 | 44.5697 | 6.165% | 44.84 | Sep | 12 | 15 | ○
650FF Case 600FF with Night Ventilation | 62.1 | Oct | 18 | 17 | 66.8465 | Oct | 1 | 16 | 62.59 | Oct | 11 | 15 | 62.469 | Oct | 18 | 16 | 63.3 | Oct | 1 | 16 | 61.1332 | Oct | 1 | 15 | 61.1332 | 66.8465 | 63.0731 | 9.058% | 62.99 | Oct | 1 | 15 | ○
950FF Case 900FF with Night Ventilation | 37.1 | Oct | 1 | 17 | 36.7765 | Sep | 11 | 15 | 36.37 | Sep | 11 | 15 | 36.6805 | Sep | 11 | 16 | 36.4 | Aug | 5 | 16 | 36.1267 | Sep | 11 | 16 | 36.1267 | 37.1 | 36.5756 | 2.661% | 37.33 | Sep | 11 | 15 | 23.63%
680FF Case 600FF with Increased Insulation | 72.5 | Jan | 22 | 17 | 78.5143 | Jan | 22 | 16 | 74.97 | Oct | 12 | 15 | 70.1447 | Jan | 22 | 16 | 72.2 | Oct | 12 | 16 | 69.7742 | Jan | 22 | 16 | 69.7742 | 78.5143 | 73.0172 | 11.97% | 72.36 | Oct | 18 | 16 | ○
980FF Case 900FF with Increased Insulation | 49.7 | Oct | 1 | 17 | 52.2464 | Sep | 12 | 15 | 52.81 | Oct | 21 | 14 | 49.6221 | Sep | 12 | 16 | 50.2 | Sep | 12 | 15 | 48.5406 | Sep | 12 | 15 | 48.5406 | 52.81 | 50.5198 | 8.451% | 51.03 | Sep | 12 | 15 | ○
960 Sunspace |  |  |  |  | 48.9033 | Oct | 2 | 16 | 53.18 | Oct | 20 | 14 | 49.8773 | Oct | 12 | 15 | 49.5 | Oct | 12 | 15 | 48.0966 | Oct | 12 | 15 | 48.0966 | 53.18 | 49.9114 | 10.18%
MINIMUM ANNUAL HOURLY INTEGRATED ZONE TEMPERATURE
Case: Simulation Model:; kW: BSIMAC; kW: CSE; kW: DeST; kW: EnergyPlus; kW: ESP-r; kW: TRNSYS; Min kW: Example Result Statistics |  |  | Tested Prg
Min kW: Min; Max kW: Max; Mean kW: Mean | (Max-Min)/
Case | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | T (°C) | T (°C) | Mean** (%) | T (°C) | Mo. | Day | Hr
600FF - Low Mass with S. Windows | -9.9 | Nov | 26 | 8 | -12.8904 | Feb | 9 | 7 | -13.52 | Feb | 9 | 6 | -12.5613 | Feb | 9 | 7 | -13.5 | Feb | 9 | 7 | -13.8442 | Feb | 9 | 7 | -13.8442 | -9.9 | -12.7026 | 31.05% | -13.79 | Feb | 9 | 7 | ○
900FF - High Mass with S. Windows | 0.6 | Feb | 8 | 11 | 2.1647 | Feb | 9 | 7 | 1.31 | Feb | 9 | 7 | 1.2424 | Feb | 9 | 7 | 1.6 | Feb | 9 | 7 | 0.63931 | Feb | 9 | 7 | 0.6 | 2.1647 | 1.2594 | 124.2% | 0.8 | Feb | 9 | 7 | ○
650FF Case 600FF with Night Ventilation | -16.7 | Dec | 31 | 24 | -17.7616 | Jan | 1 | 1 | -17.37 | Dec | 30 | 23 | -17.0758 | Dec | 31 | 24 | -17.5 | Jan | 1 | 1 | -17.5067 | Dec | 31 | 24 | -17.7616 | -16.7 | -17.319 | 6.129% | -17.47 | Dec | 31 | 24 | ○
950FF Case 900FF with Night Ventilation | -13.2 | Dec | 31 | 24 | -13.2443 | Jan | 1 | 1 | -13.36 | Dec | 30 | 23 | -12.8122 | Feb | 9 | 7 | -12.5 | Feb | 9 | 6 | -12.7995 | Feb | 9 | 6 | -13.36 | -12.5 | -12.986 | 6.623% | -13.42 | Dec | 31 | 24 | -6.977%
680FF Case 600FF with Increased Insulation | -5.7 | Feb | 8 | 11 | -6.1966 | Feb | 9 | 7 | -6.89 | Feb | 9 | 7 | -7.0523 | Feb | 9 | 7 | -7.2 | Feb | 9 | 7 | -8.0736 | Feb | 9 | 7 | -8.0736 | -5.7 | -6.8521 | 34.64% | -8.01 | Feb | 9 | 7 | ○
980FF Case 900FF with Increased Insulation | 7.3 | Feb | 8 | 11 | 12.5361 | Nov | 4 | 7 | 12.4 | Nov | 5 | 6 | 9.917 | Nov | 4 | 7 | 10.5 | Nov | 4 | 8 | 9.4717 | Nov | 4 | 7 | 7.3 | 12.5361 | 10.3541 | 50.57% | 10.44 | Nov | 4 | 7 | ○
960 Sunspace |  |  |  |  | 8.0165 | Feb | 9 | 8 | 6.74 | Feb | 9 | 6 | 5.0931 | Feb | 9 | 7 | 5 | Feb | 9 | 7 | 4.2376 | Feb | 9 | 7 | 4.2376 | 8.0165 | 5.8174 | 64.96%
AVERAGE ANNUAL HOURLY INTEGRATED ZONE TEMPERATURE
Case: Simulation Model:; kW: BSIMAC; kW: CSE; kW: DeST; kW: EnergyPlus; kW: ESP-r; kW: TRNSYS; Min kW: Example Result Statistics |  |  | Tested Prg
Min kW: Min; Max kW: Max; Mean kW: Mean | (Max-Min)/
Case: Case; kW: T (°C); kW: T (°C); kW: T (°C); kW: T (°C); kW: T (°C); kW: T (°C); Min kW: T (°C); Max kW: T (°C); Mean kW: T (°C) | Mean** (%) | T (°C)
Case: 600FF - Low Mass with S. Windows; kW: 26.1; kW: 25.5736; kW: 25.26; kW: 24.9173; kW: 25.26; kW: 24.2578; Min kW: 24.2578; Max kW: 26.1; Mean kW: 25.2281 | 7.302% | 24.8 |  |  |  | ○
Case: 900FF - High Mass with S. Windows; kW: 25.5; kW: 25.6921; kW: 25.25; kW: 25.1213; kW: 25.34; kW: 24.4623; Min kW: 24.4623; Max kW: 25.6921; Mean kW: 25.2276 | 4.875% | 24.93 |  |  |  | ○
Case: 650FF Case 600FF with Night Ventilation; kW: 17.6; kW: 18.4599; kW: 18.04; kW: 18.4195; kW: 18.93; kW: 18.402; Min kW: 17.6; Max kW: 18.93; Mean kW: 18.3086 | 7.264% | 18.71 |  |  |  | ○
Case: 950FF Case 900FF with Night Ventilation; kW: 15; kW: 14.7096; kW: 14.35; kW: 14.789; kW: 14.78; kW: 14.6786; Min kW: 14.35; Max kW: 15; Mean kW: 14.7179 | 4.416% | 14.77 |  |  |  | ○
Case: 680FF Case 600FF with Increased Insulation; kW: 31.8; kW: 33.1103; kW: 33.3; kW: 30.9584; kW: 31.71; kW: 30.1869; Min kW: 30.1869; Max kW: 33.3; Mean kW: 31.8443 | 9.776% | 31.4 |  |  |  | ○
Case: 980FF Case 900FF with Increased Insulation; kW: 30.7; kW: 33.2952; kW: 33.3; kW: 31.1618; kW: 31.84; kW: 30.492; Min kW: 30.492; Max kW: 33.3; Mean kW: 31.7982 | 8.831% | 31.56 |  |  |  | ○
Case: 960 Sunspace; kW: 28.5573; kW: 29.45; kW: 27.7427; kW: 27.74; kW: 26.7976; Min kW: 26.7976; Max kW: 29.45; Mean kW: 28.0575 | 9.453%
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 3
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-6. Low Mass Basic Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Case | [6 empty] | Min | Max | Mean | Mean** (%)
610-600 Heat, S. Shade | 0.113 | 0.073669 | 0.097 | 0.050431 | 0.165 | 0.08851 | 0.050431 | 0.165 | 0.097935 | 117% | 0.0942 | ○
620-600 Heat, E&W Orient. | 0.32 | 0.10084 | 0.25 | 0.1607 | 0.1523 | 0.21543 | 0.10084 | 0.32 | 0.19988 | 109.6% | 0.248 | ○
630-620 Heat, E&W Shade | 0.553 | 0.26235 | 0.38 | 0.29847 | 0.5363 | 0.4196 | 0.26235 | 0.553 | 0.40829 | 71.19% | 0.4053 | ○
640-600 Heat, Htg. Setback | -1.368 | -1.5895 | -1.428 | -1.6625 | -1.7076 | -1.8508 | -1.8508 | -1.368 | -1.6011 | 30.15% | -2.017 | -34.42%
660-600 Heat, Low-E Win. | -0.476 | -0.3908 | -0.226 | -0.61764 | -0.575 | -0.71389 | -0.71389 | -0.226 | -0.49989 | 97.6% | -0.5082 | ○
670-600 Heat, 1-Pane Win. | 1.434 | 1.3074 | 1.526 | 1.2918 | 1.613 | 1.6363 | 1.2918 | 1.6363 | 1.4681 | 23.47% | 1.4612 | ○
680-600 Heat, > Ins. 20/27 | -1.831 | -2.2067 | -2.315 | -2.1447 | -2.2299 | -2.2173 | -2.315 | -1.831 | -2.1574 | 22.43% | -2.2355 | ○
685-600 Heat, 20/20 tstat | 0.482 | 0.58167 | 0.599 | 0.55275 | 0.5415 | 0.53862 | 0.482 | 0.599 | 0.54926 | 21.3% | 0.5887 | ○
695-685 Heat, > Ins. 20/20 | -1.823 | -2.1592 | -2.261 | -2.0752 | -2.1714 | -2.1504 | -2.261 | -1.823 | -2.1067 | 20.79% | -2.1481 | ○
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Case | [6 empty] | Min | Max | Mean | Mean** (%)
610-600 Cool, S. Shade | -1.523 | -1.5313 | -1.259 | -1.6943 | -1.9293 | -1.6627 | -1.9293 | -1.259 | -1.5999 | 41.9% | -1.4831 | ○
620-600 Cool, E&W Orient. | -1.418 | -1.8338 | -1.523 | -1.9675 | -1.9161 | -1.9389 | -1.9675 | -1.418 | -1.7662 | 31.11% | -1.8457 | ○
630-620 Cool, E&W Shade | -1.33 | -1.0589 | -1.122 | -1.2235 | -1.6504 | -1.2678 | -1.6504 | -1.0589 | -1.2754 | 46.38% | -1.2328 | ○
640-600 Cool, Htg. Setback | -0.018 | -0.26921 | -0.195 | -0.26394 | -0.2692 | -0.3023 | -0.3023 | -0.018 | -0.21961 | 129.5% | -0.3775 | -26.45%
650-600 Cool, Night Vent | -1.193 | -1.2592 | -1.246 | -1.2103 | -1.2167 | -1.1472 | -1.2592 | -1.1472 | -1.2121 | 9.246% | -1.1614 | ○
660-600 Heat, Low-E Win. | -2.808 | -2.5734 | -2.172 | -2.7955 | -2.9432 | -2.8133 | -2.9432 | -2.172 | -2.6842 | 28.73% | -2.6578 | ○
670-600 Heat, 1-Pane Win. | 0.717 | 0.66462 | 0.522 | 0.59566 | 0.3585 | 0.41828 | 0.3585 | 0.717 | 0.54601 | 65.66% | 0.217 | -39.47%
680-600 Heat, > Ins. 20/27 | 0.116 | 0.51669 | 0.5 | 0.41686 | 0.3676 | 0.53023 | 0.116 | 0.53023 | 0.4079 | 101.6% | 0.6054 | 18.15%
685-600 Heat, 20/20 tstat | 3.308 | 2.9461 | 2.806 | 3.0918 | 2.9596 | 3.0718 | 2.806 | 3.308 | 3.0305 | 16.56% | 3.0107 | ○
695-685 Heat, > Ins. 20/20 | -0.375 | 0.1149 | 0.148 | 0.052759 | 0.0276 | 0.18778 | -0.375 | 0.18778 | 0.026007 | 2164% | 0.301 | 20.12%
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Case | [6 empty] | Min | Max | Mean | Mean** (%)
610-600 Heat, S. Shade | -0.089 | 0.000526 | 0.004 | -0.012584 | 0.005 | 0.00060921 | -0.089 | 0.005 | -0.015241 | 616.7% | 0.004 | ○
620-600 Heat, E&W Orient. | -0.11 | 0.017627 | 0.033 | 0.024696 | 0.025 | 0.025699 | -0.11 | 0.033 | 0.0026702 | 5355% | 0.05 | 11.89%
630-620 Heat, E&W Shade | 0.107 | 0.001512 | 0.004 | -0.022564 | 0.006 | 0.0029619 | -0.022564 | 0.107 | 0.016485 | 786% | 0.006 | ○
640-600 Heat, Htg. Setback | 1.378 | 1.2022 | 1.623 | 1.3541 | 0.873 | 0.67965 | 0.67965 | 1.623 | 1.185 | 79.61% | 1.102 | ○
660-600 Heat, Low-E Win. | -0.635 | -0.26192 | -0.237 | -0.3733 | -0.382 | -0.40371 | -0.635 | -0.237 | -0.38216 | 104.1% | -0.335 | ○ | 0 | -0.40023 | -0.40371 | -0.38216 | 0.01327 | 0 | 0 | 6
670-600 Heat, 1-Pane Win. | 0.867 | 0.63519 | 0.777 | 0.6491 | 0.764 | 0.86207 | 0.63519 | 0.867 | 0.75906 | 30.54% | 0.68 | ○ | 7 | 0.63519 | 0.86207 | 0.75906 | 0.037066 | -5 | -17 | 7
680-600 Heat, > Ins. 20/27 | -1.129 | -1.2426 | -1.224 | -1.152 | -1.206 | -1.2442 | -1.2442 | -1.129 | -1.1996 | 9.601% | -1.111 | 15.63% | 7 | -1.2426 | -1.2329 | -1.1996 | 0.069211 | -5 | -17 | 8
685-600 Heat, 20/20 tstat | -0.086 | 0.011624 | 0.019 | 0.018741 | 0.019 | 0.015534 | -0.086 | 0.019 | -0.0003502 | 29983% | 0.028 | 8.571% | 0 | 0.011624 | 0.015534 | -0.0003502 | 0.00124 | 0 | 0 | 9
695-685 Heat, > Ins. 20/20 | -1.031 | -1.2365 | -1.199 | -1.1514 | -1.222 | -1.2567 | -1.2567 | -1.031 | -1.1828 | 19.08% | -1.133 | ○ | 7 | -1.2365 | -1.2364 | -1.1828 | 0.06368 | -5 | -17 | 1
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Case | [6 empty] | Min | Max | Mean | Mean** (%)
610-600 Cool, S. Shade | -0.184 | -0.048825 | -0.091 | -0.21703 | -0.259 | -0.17795 | -0.259 | -0.048825 | -0.16297 | 129% | -0.265 | -2.855%
620-600 Cool, E&W Orient. | -0.946 | -1.9882 | -1.467 | -1.5541 | -1.571 | -1.4575 | -1.9882 | -0.946 | -1.4973 | 69.6% | -1.373 | ○
630-620 Cool, E&W Shade | -0.583 | -0.49451 | -0.429 | -0.58526 | -0.651 | -0.63889 | -0.651 | -0.429 | -0.56361 | 39.39% | -0.605 | ○
640-600 Cool, Htg. Setback | 0 | -0.052004 | -0.057 | -0.05417 | -0.066 | -0.078665 | -0.078665 | 0 | -0.051306 | 153.3% | -0.114 | -44.92%
650-600 Cool, Night Vent | -0.002 | -0.19129 | -0.377 | -0.21342 | -0.232 | -0.24825 | -0.377 | -0.002 | -0.21066 | 178% | -0.168 | ○
660-600 Heat, Low-E Win. | -2.307 | -2.548 | -2.067 | -2.5812 | -2.663 | -2.5883 | -2.663 | -2.067 | -2.4591 | 24.24% | -2.174 | ○ | 0 | -2.079 | -2.548 | -2.4591 | -0.010291 | 0 | 0
670-600 Heat, 1-Pane Win. | 0.567 | 0.44432 | 0.417 | 0.45463 | 0.289 | 0.35556 | 0.289 | 0.567 | 0.42125 | 65.99% | 0.332 | ○ | 0 | 0.417 | 0.44432 | 0.42125 | -0.0072513 | 0 | 0
680-600 Heat, > Ins. 20/27 | 0.111 | 0.57027 | 0.439 | 0.41866 | 0.483 | 0.51086 | 0.111 | 0.57027 | 0.42213 | 108.8% | 0.419 | ○ | 0 | 0.339 | 0.57027 | 0.42213 | 0.024365 | 4 | 0
685-600 Heat, 20/20 tstat | 0.668 | 0.67846 | 0.649 | 0.7552 | 0.741 | 0.82169 | 0.649 | 0.82169 | 0.71889 | 24.02% | 0.679 | ○ | 0 | 0.649 | 0.67846 | 0.71889 | -0.014375 | 0 | 0
695-685 Heat, > Ins. 20/20 | -0.086 | 0.38129 | 0.284 | 0.22753 | 0.305 | 0.30772 | -0.086 | 0.38129 | 0.23659 | 197.5% | 0.33 | ○ | 0 | 0.161 | 0.38129 | 0.23659 | 0.026091 | 4 | 0
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-7. High Mass Basic Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
900-600 Mass, Heat | -2.324 | -2.6139 | -2.456 | -2.6607 | -2.7773 | -2.6895 | -2.7773 | -2.324 | -2.5869 | 17.52% | -2.691 | ○
910-900 Heat, S. Shade | 0.437 | 0.26879 | 0.269 | 0.29205 | 0.4825 | 0.31776 | 0.26879 | 0.4825 | 0.34452 | 62.03% | 0.3148 | ○
920-900 Heat, E&W Orient. | 1.774 | 1.5772 | 1.668 | 1.6728 | 1.715 | 1.7927 | 1.5772 | 1.7927 | 1.6999 | 12.68% | 1.7922 | ○
930-920 Heat, E&W Shade | 0.77 | 0.56758 | 0.674 | 0.6573 | 0.9779 | 0.7774 | 0.56758 | 0.9779 | 0.73736 | 55.65% | 0.7611 | ○
940-900 Heat, Htg. Setback | -0.337 | -0.51566 | -0.442 | -0.5963 | -0.57 | -0.6449 | -0.6449 | -0.337 | -0.51764 | 59.48% | -0.6878 | -13.93%
960-900 Heat, Sunspace |  | 1.1432 | 1.18 | 1.0254 | 1.0392 | 1.0455 | 1.0254 | 1.18 | 1.0866 | 14.23% | 1.2762 | 62.21%
980-900 Heat, > Ins. 20/27 | -1.006 | -1.1331 | -1.325 | -1.2527 | -1.2336 | -1.3636 | -1.3636 | -1.006 | -1.219 | 29.33% | -1.3597 | ○
985-900 Heat, 20/20 tstat | 1.075 | 0.74132 | 0.688 | 0.70563 | 0.6986 | 0.72238 | 0.688 | 1.075 | 0.77182 | 50.14% | 0.778 | ○
995-985 Heat, > Ins. 20/20 | -1.471 | -1.365 | -1.509 | -1.3628 | -1.3785 | -1.4594 | -1.509 | -1.3628 | -1.4243 | 10.26% | -1.5237 | -10.06%
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
900-600 Mass, Cool | -3.108 | -3.4493 | -3.049 | -3.5383 | -3.6741 | -3.5124 | -3.6741 | -3.049 | -3.3885 | 18.45% | -3.3292 | ○
910-900 Cool, S. Shade | -1.23 | -1.049 | -0.893 | -1.1053 | -1.2048 | -1.0763 | -1.23 | -0.893 | -1.093 | 30.83% | -1.0162 | ○
920-900 Cool, E&W Orient. | 0.414 | 0.32538 | 0.323 | 0.2421 | 0.3267 | 0.28174 | 0.2421 | 0.414 | 0.31882 | 53.92% | 0.2095 | -18.97%
930-920 Cool, E&W Shade | -0.967 | -0.71422 | -0.798 | -0.81173 | -1.1606 | -0.87711 | -1.1606 | -0.71422 | -0.88811 | 50.26% | -0.8688 | ○
940-900 Cool, Htg. Setback | -0.101 | -0.06725 | -0.04 | -0.06439 | -0.0601 | -0.06367 | -0.101 | -0.04 | -0.066068 | 92.33% | -0.0823 | ○
950-900 Cool, Night Vent | -2.128 | -1.8658 | -1.765 | -1.7818 | -1.8317 | -1.6255 | -2.128 | -1.6255 | -1.833 | 27.41% | -1.7097 | ○
960-900 Cool, Sunspace |  | -1.538 | -1.474 | -1.5816 | -1.5381 | -1.4782 | -1.5816 | -1.474 | -1.522 | 7.071% | -1.6476 | -61.3%
980-900 Heat, > Ins. 20/27 | 0.787 | 1.5314 | 1.375 | 1.2231 | 1.2868 | 1.2514 | 0.787 | 1.5314 | 1.2425 | 59.92% | 1.3242 | ○
985-900 Heat, 20/20 tstat | 4.559 | 3.7698 | 3.497 | 3.8704 | 3.7616 | 3.8463 | 3.497 | 4.559 | 3.884 | 27.34% | 3.8589 | ○
995-985 Heat, > Ins. 20/20 | 0.209 | 0.9685 | 0.891 | 0.84367 | 0.8995 | 0.95032 | 0.209 | 0.9685 | 0.79367 | 95.7% | 0.9106 | ○
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
900-600 Mass, Heat | -0.704 | -0.57684 | -0.582 | -0.51694 | -0.595 | -0.58042 | -0.704 | -0.51694 | -0.59253 | 31.57% | -0.526 | ○
910-900 Heat, S. Shade | 0.21 | 0.025635 | 0.021 | 0.011437 | 0.051 | 0.020717 | 0.011437 | 0.21 | 0.056631 | 350.6% | 0.02 | ○
920-900 Heat, E&W Orient. | 0.344 | 0.069036 | 0.06 | 0.08269 | 0.073 | 0.085796 | 0.06 | 0.344 | 0.11909 | 238.5% | 0.076 | ○
930-920 Heat, E&W Shade | 0.073 | 0.024542 | 0.036 | 0.014719 | 0.059 | 0.03614 | 0.014719 | 0.073 | 0.040567 | 143.7% | 0.033 | ○
940-900 Heat, Htg. Setback | 1.331 | 0.60852 | 1.206 | 0.45528 | 0.489 | 0.62635 | 0.45528 | 1.331 | 0.78602 | 111.4% | 0.807 | ○
960-900 Heat, Sunspace |  | -0.31135 | -0.368 | -0.42812 | -0.432 | -0.47808 | -0.47808 | -0.31135 | -0.40351 | 41.32% | -0.374 | ○
980-900 Heat, > Ins. 20/27 | -0.858 | -1.1896 | -1.071 | -1.1497 | -1.16 | -1.1863 | -1.1896 | -0.858 | -1.1024 | 30.08% | -1.026 | ○ | 0 | -1.1896 | -1.0855 | -1.1024 | 0.16572 | 0 | 0 | 7
985-900 Heat, 20/20 tstat | 0.203 | 0.008773 | 0.005 | 0.0079536 | 0.009 | 0.0069624 | 0.005 | 0.203 | 0.040115 | 493.6% | 0.006 | ○ | -1 | 0.008773 | 0.0069624 | 0.040115 | -0.0026598 | 0 | 0 | 8
995-985 Heat, > Ins. 20/20 | -1.043 | -1.0826 | -0.996 | -1.0733 | -1.082 | -1.1235 | -1.1235 | -0.996 | -1.0667 | 11.95% | -0.981 | 11.77% | 0 | -1.0826 | -1.0744 | -1.0667 | 0.091588 | 0 | 0 | 1
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
900-600 Mass, Cool | -2.611 | -3.1046 | -2.866 | -3.3111 | -3.297 | -3.1057 | -3.3111 | -2.611 | -3.0492 | 22.96% | -2.791 | ○
910-900 Cool, S. Shade | -0.546 | -0.65436 | -0.453 | -0.81835 | -0.684 | -0.85903 | -0.85903 | -0.453 | -0.66912 | 60.68% | -0.682 | ○
920-900 Cool, E&W Orient. | 0.442 | -0.31975 | 0.154 | 0.21988 | 0.203 | 0.21408 | -0.31975 | 0.442 | 0.1522 | 500.5% | 0.091 | ○
930-920 Cool, E&W Shade | -0.429 | -0.39486 | -0.375 | -0.47881 | -0.605 | -0.54103 | -0.605 | -0.375 | -0.47062 | 48.87% | -0.473 | ○
940-900 Cool, Htg. Setback | 0.119 | 0 | 0 | -0.00048524 | -0.005 | -0.0024478 | -0.005 | 0.119 | 0.018511 | 669.9% | 0 | ○
950-900 Cool, Night Vent | -0.673 | -1.0129 | -0.502 | -0.65292 | -0.694 | -0.70368 | -1.0129 | -0.502 | -0.70642 | 72.33% | -0.481 | 4.11%
960-900 Cool, Sunspace |  | -1.9993 | -1.189 | -1.5605 | -1.493 | -1.6016 | -1.9993 | -1.189 | -1.5687 | 51.66% | -1.46 | ○
980-900 Heat, > Ins. 20/27 | 0.345 | 0.29156 | 0.374 | 0.40968 | 0.445 | 0.37249 | 0.29156 | 0.445 | 0.37295 | 41.14% | 0.339 | ○ | 0 | 0.374 | 0.29156 | 0.37295 | -0.055353 | 7 | 0
985-900 Heat, 20/20 tstat | 0.938 | 0.84883 | 0.652 | 0.87434 | 0.84 | 0.94464 | 0.652 | 0.94464 | 0.84963 | 34.44% | 0.698 | ○ | 0 | 0.652 | 0.84883 | 0.84963 | -0.0098063 | -10 | 0
995-985 Heat, > Ins. 20/20 | 0.152 | -0.001482 | 0.107 | 0.26266 | 0.218 | 0.2302 | -0.001482 | 0.26266 | 0.1614 | 163.7% | 0.127 | ○ | 1 | 0.107 | -0.001482 | 0.1614 | -0.037989 | 21 | 1
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 4
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-8. Low Mass In-Depth (Cases 195 thru 320) Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
200-195 Surface Convection | 0.824 | 0.82337 | 1.069 | 1.0358 | 0.9695 | 1.0489 | 0.82337 | 1.069 | 0.96176 | 25.54% | 1.0135 | ○
210-200 Ext IR (Int IR "off") | 0.586 | 1.1529 | 1.305 | 0.94118 | 1.3967 | 1.2866 | 0.586 | 1.3967 | 1.1114 | 72.94% | 1.2017 | ○
220-215 Ext IR (Int IR "on") | 0.725 | 1.3597 | 1.481 | 1.0497 | 1.5446 | 1.4244 | 0.725 | 1.5446 | 1.2641 | 64.84% | 1.3945 | ○
215-200 Int IR (Ext IR "off") | 0.611 | 0.49316 | 0.471 | 0.30004 | 0.2607 | 0.30051 | 0.2607 | 0.611 | 0.40607 | 86.27% | 0.4695 | ○
220-210 Int IR (Ext IR "on") | 0.75 | 0.70003 | 0.647 | 0.40857 | 0.4086 | 0.43834 | 0.40857 | 0.75 | 0.55876 | 61.1% | 0.6623 | ○
230-220 Infiltration | 3.474 | 3.146 | 3.239 | 3.4747 | 3.2128 | 3.3665 | 3.146 | 3.4747 | 3.3188 | 9.904% | 3.3937 | ○
240-220 Internal Gains | -1.261 | -1.2237 | -1.234 | -1.1758 | -1.1864 | -1.2106 | -1.261 | -1.1758 | -1.2153 | 7.014% | -1.2224 | ○
250-220 Ext Solar Abs. | -1.644 | -1.6225 | -1.805 | -1.556 | -1.7907 | -1.7631 | -1.805 | -1.556 | -1.6969 | 14.67% | -1.7274 | ○
270-220 South Windows |  | -2.3199 | -2.905 | -2.0698 | -2.1493 | -2.2367 | -2.905 | -2.0698 | -2.3361 | 35.75% | -2.3737 | ○
280-270 Cavity Albedo |  | 0.17846 | 0.346 | 0.18472 | 0.1617 | 0.23873 | 0.1617 | 0.346 | 0.22192 | 83.05% | 0.2982 | ○
320-270 Thermostat |  | -0.66901 | -0.674 | -0.61416 | -0.6065 | -0.60003 | -0.674 | -0.60003 | -0.63274 | 11.69% | -0.6546 | ○
290-270 South Shading |  | 0.077715 | 0.108 | 0.039046 | 0.1683 | 0.09362 | 0.039046 | 0.1683 | 0.097336 | 132.8% | 0.101 | ○
300-270 E&W Windows |  | -0.028118 | 0.187 | 0.039197 | 0.0915 | 0.09447 | -0.028118 | 0.187 | 0.07681 | 280.1% | 0.1285 | ○
310-300 E&W Shading |  | 0.26199 | 0.386 | 0.26662 | 0.5717 | 0.43695 | 0.26199 | 0.5717 | 0.38465 | 80.52% | 0.4126 | ○
ANNUAL SENSIBLE COOLING [MWh]
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
200-195 Surface Convection | 0.127 | 0.19471 | 0.207 | 0.20256 | 0.1894 | 0.19691 | 0.127 | 0.207 | 0.18626 | 42.95% | 0.2046 | ○
210-200 Ext IR (Int IR "off") | -0.151 | -0.29717 | -0.339 | -0.25418 | -0.2819 | -0.32926 | -0.339 | -0.151 | -0.27542 | 68.26% | -0.3336 | ○
220-215 Ext IR (Int IR "on") | -0.149 | -0.33519 | -0.372 | -0.26756 | -0.3186 | -0.35281 | -0.372 | -0.149 | -0.29919 | 74.53% | -0.3632 | ○
215-200 Int IR (Ext IR "off") | 0.113 | 0.14556 | 0.087 | 0.063388 | 0.0944 | 0.062024 | 0.062024 | 0.14556 | 0.094228 | 88.65% | 0.0878 | ○
220-210 Int IR (Ext IR "on") | 0.115 | 0.10753 | 0.054 | 0.050007 | 0.0577 | 0.038475 | 0.038475 | 0.115 | 0.070452 | 108.6% | 0.0582 | ○
230-220 Infiltration | 0.381 | 0.38074 | 0.379 | 0.38131 | 0.3788 | 0.39898 | 0.3788 | 0.39898 | 0.3833 | 5.265% | 0.4054 | 31.81%
240-220 Internal Gains | 0.484 | 0.37177 | 0.326 | 0.36884 | 0.3456 | 0.33612 | 0.326 | 0.484 | 0.37206 | 42.47% | 0.3324 | ○
250-220 Ext Solar Abs. | 2.809 | 2.8184 | 2.921 | 2.5717 | 2.8906 | 2.4062 | 2.4062 | 2.921 | 2.7361 | 18.82% | 2.4789 | ○
270-220 South Windows |  | 6.6602 | 6.148 | 6.9116 | 6.7324 | 6.7908 | 6.148 | 6.9116 | 6.6486 | 11.49% | 6.7575 | ○
280-270 Cavity Albedo |  | -2.2745 | -2.483 | -2.3386 | -2.1028 | -2.4804 | -2.483 | -2.1028 | -2.3359 | 16.28% | -2.2697 | ○
320-270 Thermostat |  | -2.4123 | -2.278 | -2.5356 | -2.3955 | -2.5008 | -2.5356 | -2.278 | -2.4244 | 10.62% | -2.4577 | ○
290-270 South Shading |  | -1.6611 | -1.388 | -1.779 | -1.988 | -1.8273 | -1.988 | -1.388 | -1.7287 | 34.71% | -1.6116 | ○
300-270 E&W Windows |  | -2.2158 | -1.893 | -2.3695 | -2.2705 | -2.3755 | -2.3755 | -1.893 | -2.2249 | 21.69% | -2.2304 | ○
310-300 E&W Shading |  | -1.3032 | -1.403 | -1.4825 | -1.9102 | -1.5887 | -1.9102 | -1.3032 | -1.5375 | 39.48% | -1.5437 | ○
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
200-195 Surface Convection | 0.47 | 0.43534 | 0.509 | 0.54692 | 0.473 | 0.5568 | 0.43534 | 0.5568 | 0.49851 | 24.37% | 0.452 | ○
210-200 Ext IR (Int IR "off") | 0.102 | 0.40294 | 0.297 | 0.22323 | 0.396 | 0.39706 | 0.102 | 0.40294 | 0.30304 | 99.31% | 0.319 | ○
220-215 Ext IR (Int IR "on") | 0.11 | 0.41938 | 0.343 | 0.21421 | 0.398 | 0.3892 | 0.11 | 0.41938 | 0.3123 | 99.07% | 0.327 | ○
215-200 Int IR (Ext IR "off") | 0.249 | 0.19396 | 0.212 | 0.13649 | 0.115 | 0.13665 | 0.115 | 0.249 | 0.17385 | 77.08% | 0.222 | ○
220-210 Int IR (Ext IR "on") | 0.257 | 0.2104 | 0.258 | 0.12747 | 0.117 | 0.12878 | 0.117 | 0.258 | 0.18311 | 77% | 0.23 | ○
230-220 Infiltration | 1.588 | 1.2935 | 1.36 | 1.6241 | 1.372 | 1.4367 | 1.2935 | 1.6241 | 1.4457 | 22.86% | 1.473 | ○
240-220 Internal Gains | -0.2 | -0.18795 | -0.178 | -0.18492 | -0.183 | -0.18548 | -0.2 | -0.178 | -0.18656 | 11.79% | -0.178 | ○
250-220 Ext Solar Abs. | 0 | -0.002311 | -0.008 | -0.0046183 | -0.008 | -0.0042134 | -0.008 | 0 | -0.0045238 | 176.8% | -0.015 | -87.5%
270-220 South Windows |  | -0.228 | -0.303 | -0.09541 | -0.04 | -0.035333 | -0.303 | -0.035333 | -0.14035 | 190.7% | -0.066 | ○
280-270 Cavity Albedo |  | 0.000866 | 0.008 | 0.005384 | 0.004 | 0.005441 | 0.000866 | 0.008 | 0.0047382 | 150.6% | 0.019 | 154.2%
320-270 Thermostat |  | -0.002429 | -0.014 | -0.023142 | -0.015 | -0.0097238 | -0.023142 | -0.002429 | -0.012859 | 161.1% | -0.026 | -13.8%
290-270 South Shading |  | 7.1e-05 | 0.001 | -0.013189 | 0.002 | 0.00016606 | -0.013189 | 0.002 | -0.0019905 | 763.1% | 0.002 | ○
300-270 E&W Windows |  | 0.002675 | 0.029 | 0.0065091 | 0.018 | 0.010408 | 0.002675 | 0.029 | 0.013318 | 197.7% | 0.025 | ○
310-300 E&W Shading |  | 0.00082 | 0.003 | -0.023064 | 0.005 | 0.0026624 | -0.023064 | 0.005 | -0.0023163 | 1212% | 0.007 | 7.127%
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
200-195 Surface Convection | 0.153 | 0.22092 | 0.266 | 0.26648 | 0.254 | 0.26541 | 0.153 | 0.26648 | 0.23764 | 47.75% | 0.245 | ○
210-200 Ext IR (Int IR "off") | -0.078 | -0.26955 | -0.302 | -0.22309 | -0.321 | -0.37477 | -0.37477 | -0.078 | -0.2614 | 113.5% | -0.313 | ○
220-215 Ext IR (Int IR "on") | -0.057 | -0.26079 | -0.346 | -0.2159 | -0.354 | -0.38409 | -0.38409 | -0.057 | -0.26963 | 121.3% | -0.327 | ○
215-200 Int IR (Ext IR "off") | 0.122 | 0.15407 | 0.147 | 0.092921 | 0.168 | 0.093176 | 0.092921 | 0.168 | 0.12953 | 57.96% | 0.123 | ○
220-210 Int IR (Ext IR "on") | 0.143 | 0.16283 | 0.103 | 0.1001 | 0.135 | 0.083849 | 0.083849 | 0.16283 | 0.1213 | 65.12% | 0.109 | ○
230-220 Infiltration | 0.658 | 0.61968 | 0.694 | 0.6564 | 0.689 | 0.72555 | 0.61968 | 0.72555 | 0.67377 | 15.71% | 0.714 | ○
240-220 Internal Gains | 0.198 | 0.18623 | 0.178 | 0.18145 | 0.18 | 0.18157 | 0.178 | 0.198 | 0.18421 | 10.86% | 0.177 | -5%
250-220 Ext Solar Abs. | 1.577 | 1.6815 | 1.711 | 1.6821 | 2.022 | 1.72 | 1.577 | 2.022 | 1.7323 | 25.69% | 1.717 | ○
270-220 South Windows |  | 5.9025 | 4.792 | 5.6543 | 5.601 | 5.6695 | 4.792 | 5.9025 | 5.5239 | 20.1% | 5.022 | ○
280-270 Cavity Albedo |  | -2.2459 | -2.064 | -2.1116 | -1.937 | -2.2376 | -2.2459 | -1.937 | -2.1192 | 14.58% | -1.875 | 20.07%
320-270 Thermostat |  | -0.53772 | -0.528 | -0.62971 | -0.62 | -0.68806 | -0.68806 | -0.528 | -0.6007 | 26.65% | -0.604 | ○
290-270 South Shading |  | -0.13883 | -0.093 | -0.24426 | -0.202 | -0.23557 | -0.24426 | -0.093 | -0.18273 | 82.78% | -0.249 | -3.131%
300-270 E&W Windows |  | -2.8478 | -2.137 | -2.3633 | -2.392 | -2.3592 | -2.8478 | -2.137 | -2.4199 | 29.38% | -2.116 | 2.954%
310-300 E&W Shading |  | -0.36725 | -0.443 | -0.50594 | -0.603 | -0.57679 | -0.603 | -0.36725 | -0.4992 | 47.23% | -0.548 | ○
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 5
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-9. Low Mass In-Depth (Cases 395 thru 440) Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
400-395 Surf. Conv. & IR | 1.341 | 1.6808 | 1.902 | 1.7066 | 1.7443 | 1.8611 | 1.341 | 1.902 | 1.706 | 32.88% | 1.8521 | ○
410-400 Infiltration | 1.724 | 1.5093 | 1.614 | 1.7325 | 1.6022 | 1.6757 | 1.5093 | 1.7325 | 1.643 | 13.59% | 1.6881 | ○
420-410 Internal Gains | -1.231 | -1.2106 | -1.228 | -1.1745 | -1.1852 | -1.2086 | -1.231 | -1.1745 | -1.2063 | 4.681% | -1.2169 | ○
430-420 Ext Solar Abs. | -1.228 | -1.3804 | -1.479 | -1.2857 | -1.4821 | -1.3858 | -1.4821 | -1.228 | -1.3735 | 18.5% | -1.4093 | ○
600-430 South Windows | -1.121 | -1.4613 | -1.907 | -1.2958 | -1.1829 | -1.347 | -1.907 | -1.121 | -1.3858 | 56.72% | -1.4692 | ○
440-600 Cavity Albedo |  | 0.16318 | 0.283 | 0.17569 | 0.1419 | 0.21713 | 0.1419 | 0.283 | 0.19618 | 71.92% | 0.2533 | ○
450-600 Const Int&Ext Surf Coefs | -0.307 | -0.0023157 | -0.672 | -0.3619 | -0.5117 | -0.63264 | -0.672 | -0.0023157 | -0.41459 | 161.5% | -0.6509 | ○
460-600 Const Int Surf Coefs | -0.222 | 0.062755 | -0.174 | -0.13062 | -0.0995 | -0.21378 | -0.222 | 0.062755 | -0.12952 | 219.8% | -0.253 | -10.89%
460-450 Auto Ext Surf Heat Transf | 0.085 | 0.065071 | 0.498 | 0.23127 | 0.4122 | 0.41886 | 0.065071 | 0.498 | 0.28507 | 151.9% | 0.3979 | ○
470-600 Const Ext Surf Coefs | -0.008 | -0.093264 | -0.507 | -0.23051 | -0.4023 | -0.42893 | -0.507 | -0.008 | -0.27833 | 179.3% | -0.4014 | ○
470-450 Auto Int Surf Heat Transf | 0.299 | -0.090948 | 0.165 | 0.13138 | 0.1094 | 0.20371 | -0.090948 | 0.299 | 0.13626 | 286.2% | 0.2495 | ○
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
400-395 Surf. Conv. & IR | 0.042 | 0.015542 | 0.011 | 0.020185 | 0.0189 | 0.0091667 | 0.0091667 | 0.042 | 0.019466 | 168.7% | 0.0104 | ○
410-400 Infiltration | 0.033 | 0.025188 | 0.024 | 0.026703 | 0.0279 | 0.022437 | 0.022437 | 0.033 | 0.026538 | 39.8% | 0.0244 | ○
420-410 Internal Gains | 0.132 | 0.092126 | 0.078 | 0.095302 | 0.0896 | 0.074316 | 0.074316 | 0.132 | 0.093557 | 61.66% | 0.0774 | ○
430-420 Ext Solar Abs. | 0.856 | 0.76554 | 0.825 | 0.70305 | 0.8108 | 0.62959 | 0.62959 | 0.856 | 0.765 | 29.6% | 0.6331 | ○
600-430 South Windows | 4.738 | 5.007 | 4.488 | 5.1714 | 5.2091 | 5.0405 | 4.488 | 5.2091 | 4.9423 | 14.59% | 5.0397 | ○
440-600 Cavity Albedo |  | -1.9278 | -1.974 | -1.942 | -1.7477 | -2.0384 | -2.0384 | -1.7477 | -1.926 | 15.09% | -1.8663 | ○
450-600 Const Int&Ext Surf Coefs | 0.35 | -0.22415 | 0.729 | 0.48022 | 0.4514 | 0.75118 | -0.22415 | 0.75118 | 0.42294 | 230.6% | 0.8835 | 13.57%
460-600 Const Int Surf Coefs | 0.438 | 0.026684 | 0.497 | 0.44757 | 0.5673 | 0.46383 | 0.026684 | 0.5673 | 0.40673 | 132.9% | 0.5682 | 0.1665%
460-450 Auto Ext Surf Heat Transf | 0.088 | 0.25083 | -0.232 | -0.03265 | 0.1159 | -0.28735 | -0.28735 | 0.25083 | -0.016211 | 3320% | -0.3153 | -5.193%
470-600 Const Ext Surf Coefs | 0.165 | -0.26923 | 0.217 | 0.0023448 | -0.1564 | 0.27637 | -0.26923 | 0.27637 | 0.039181 | 1393% | 0.2989 | 4.129%
470-450 Auto Int Surf Heat Transf | -0.185 | -0.045084 | -0.512 | -0.47787 | -0.6078 | -0.47481 | -0.6078 | -0.045084 | -0.38376 | 146.6% | -0.5846 | ○
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
400-395 Surf. Conv. & IR | 0.611 | 0.68193 | 0.778 | 0.74028 | 0.698 | 0.71723 | 0.611 | 0.778 | 0.70441 | 23.71% | 0.694 | ○
410-400 Infiltration | 0.779 | 0.60131 | 0.68 | 0.81203 | 0.685 | 0.71836 | 0.60131 | 0.81203 | 0.71262 | 29.57% | 0.736 | ○
420-410 Internal Gains | -0.2 | -0.18445 | -0.178 | -0.18492 | -0.183 | -0.18548 | -0.2 | -0.178 | -0.18597 | 11.83% | -0.178 | ○
430-420 Ext Solar Abs. | 0.162 | -0.002354 | -0.005 | -0.002869 | -0.005 | -0.0026383 | -0.005 | 0.162 | 0.024023 | 695.2% | -0.009 | -2.395%
600-430 South Windows | -0.045 | -0.23365 | -0.325 | -0.11183 | -0.057 | -0.049923 | -0.325 | -0.045 | -0.13707 | 204.3% | -0.085 | ○
440-600 Cavity Albedo |  | 0.006973 | 0.025 | 0.014228 | 0.009 | 0.015399 | 0.006973 | 0.025 | 0.01412 | 127.7% | 0.029 | 22.19%
450-600 Const Int&Ext Surf Coefs | -0.266 | -0.041917 | -0.282 | -0.10461 | -0.186 | -0.32158 | -0.32158 | -0.041917 | -0.20035 | 139.6% | -0.162 | ○ | 0 | -0.26723 | -0.25907 | -0.20035 | 0.009879 | 0 | 0 | 41
460-600 Const Int Surf Coefs | -0.2 | -0.04888 | -0.055 | -0.11337 | -0.127 | -0.19922 | -0.2 | -0.04888 | -0.12391 | 122% | -0.082 | ○ | 0 | -0.04888 | -0.19922 | -0.12391 | -0.044829 | 0 | 0 | 42
460-450 Auto Ext Surf Heat Transf | 0.066 | -0.006963 | 0.227 | -0.0087666 | 0.059 | 0.12236 | -0.0087666 | 0.227 | 0.076438 | 308.4% | 0.08 | ○ | 0 | 0.21835 | 0.059851 | 0.076438 | -0.054708 | 0 | 0 | 1
470-600 Const Ext Surf Coefs | -0.137 | -0.019557 | -0.228 | 0.0023118 | -0.059 | -0.1274 | -0.228 | 0.0023118 | -0.094774 | 243% | -0.086 | ○ | 0 | -0.21323 | -0.1274 | -0.094774 | 0.031052 | 0 | 0 | 43
470-450 Auto Int Surf Heat Transf | 0.129 | 0.02236 | 0.054 | 0.10692 | 0.127 | 0.19418 | 0.02236 | 0.19418 | 0.10558 | 162.7% | 0.076 | ○ | 0 | 0.054 | 0.13167 | 0.10558 | 0.021173 | 0 | 0 | 2
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
400-395 Surf. Conv. & IR | 0.251 | 0.13615 | 0.149 | 0.22943 | 0.162 | 0.10678 | 0.10678 | 0.251 | 0.17239 | 83.66% | 0.163 | ○
410-400 Infiltration | 0.213 | 0.20623 | 0.252 | 0.22094 | 0.168 | 0.2317 | 0.168 | 0.252 | 0.21531 | 39.01% | 0.246 | ○
420-410 Internal Gains | 0.197 | 0.20865 | 0.208 | 0.20469 | 0.212 | 0.21039 | 0.197 | 0.212 | 0.20679 | 7.254% | 0.195 | -13.33%
430-420 Ext Solar Abs. | 0.959 | 0.93129 | 0.923 | 0.89683 | 1.038 | 0.89001 | 0.89001 | 1.038 | 0.93969 | 15.75% | 0.791 | -66.9%
600-430 South Windows | 3.483 | 4.6412 | 3.582 | 4.4222 | 4.319 | 4.3417 | 3.483 | 4.6412 | 4.1315 | 28.03% | 3.932 | ○
440-600 Cavity Albedo |  | -1.8155 | -1.656 | -1.6656 | -1.514 | -1.7382 | -1.8155 | -1.514 | -1.6778 | 17.97% | -1.425 | 29.52%
450-600 Const Int&Ext Surf Coefs | 0.162 | -0.30121 | 0.641 | 0.11476 | 0.308 | 0.26769 | -0.30121 | 0.641 | 0.19871 | 474.2% | 0.79 | 15.81% | 0 | 0.39 | 0.020008 | 0.19871 | -0.065073
460-600 Const Int Surf Coefs | 0.154 | -0.23813 | 0.48 | 0.0226 | 0.111 | 0.023202 | -0.23813 | 0.48 | 0.092113 | 779.6% | 0.543 | 8.773% | 0 | 0.382 | -0.10682 | 0.092113 | -0.082573
460-450 Auto Ext Surf Heat Transf | -0.008 | 0.063083 | -0.161 | -0.09216 | -0.197 | -0.24449 | -0.24449 | 0.063083 | -0.10659 | 288.5% | -0.247 | -0.8164% | 0 | -0.008 | -0.12683 | -0.10659 | -0.0175
470-600 Const Ext Surf Coefs | 0.045 | -0.093327 | 0.148 | 0.092071 | 0.214 | 0.27425 | -0.093327 | 0.27425 | 0.11333 | 324.3% | 0.159 | ○ | 0 | 0.148 | -0.037353 | 0.11333 | -0.033448
470-450 Auto Int Surf Heat Transf | -0.117 | 0.20788 | -0.493 | -0.022689 | -0.094 | 0.0065584 | -0.493 | 0.20788 | -0.085375 | 821% | -0.631 | -19.69% | 0 | -0.242 | -0.057361 | -0.085375 | 0.031625
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-10. High Mass Basic and In-Depth Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
800-430 Mass, w/ High Cond. Wall | -0.03 | -0.54834 | -0.551 | -0.50457 | -0.5651 | -0.48107 | -0.5651 | -0.03 | -0.44668 | 119.8% | -0.4966 | ○
900-800 Himass, S. Win. | -3.415 | -3.5268 | -3.812 | -3.4519 | -3.3951 | -3.5554 | -3.812 | -3.3951 | -3.526 | 11.82% | -3.6636 | ○
900-810 Himass, Int. Sol. Abs. |  | -0.65862 | -0.863 | -0.67814 | -0.6003 | -0.79572 | -0.863 | -0.6003 | -0.71916 | 36.53% | -0.7783 | ○
910-610 Mass, w/ S. Shade | -2 | -2.4187 | -2.284 | -2.4191 | -2.4598 | -2.4603 | -2.4603 | -2 | -2.3403 | 19.67% | -2.4704 | -2.201%
920-620 Mass, w/ E&W Win. | -0.87 | -1.1375 | -1.038 | -1.1486 | -1.2146 | -1.1123 | -1.2146 | -0.87 | -1.0868 | 31.71% | -1.1468 | ○
930-630 Mass w/ E&W Shade | -0.653 | -0.8323 | -0.744 | -0.78974 | -0.773 | -0.75448 | -0.8323 | -0.653 | -0.75775 | 23.66% | -0.791 | ○
940-640 Mass, w/ Htg. Setback | -1.293 | -1.54 | -1.47 | -1.5945 | -1.6397 | -1.4836 | -1.6397 | -1.293 | -1.5035 | 23.06% | -1.3618 | ○
980-680 Mass, w/ Insulation 20/27 | -1.499 | -1.5403 | -1.466 | -1.7687 | -1.781 | -1.8358 | -1.8358 | -1.466 | -1.6485 | 22.43% | -1.8152 | ○
985-685 Mass, w/ 20/20 Tstat | -1.731 | -2.4542 | -2.367 | -2.5078 | -2.6202 | -2.5058 | -2.6202 | -1.731 | -2.3643 | 37.61% | -2.5017 | ○
995-695 Mass, w/ Insulation 20/20 | -1.379 | -1.6601 | -1.615 | -1.7954 | -1.8273 | -1.8147 | -1.8273 | -1.379 | -1.6819 | 26.65% | -1.8773 | -11.15%
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
800-430 Mass, w/ High Cond. Wall | -0.611 | -0.52633 | -0.582 | -0.48209 | -0.5613 | -0.45694 | -0.611 | -0.45694 | -0.53661 | 28.71% | -0.4819 | ○
900-800 Himass, S. Win. | 2.241 | 2.084 | 2.021 | 2.1152 | 2.0963 | 1.985 | 1.985 | 2.241 | 2.0904 | 12.24% | 2.1924 | ○
900-810 Himass, Int. Sol. Abs. |  | 0.98312 | 1.026 | 0.98095 | 0.8821 | 0.97261 | 0.8821 | 1.026 | 0.96896 | 14.85% | 0.9952 | ○
910-610 Mass, w/ S. Shade | -2.815 | -2.9669 | -2.683 | -2.9493 | -2.9496 | -2.9259 | -2.9669 | -2.683 | -2.8816 | 9.853% | -2.8623 | ○
920-620 Mass, w/ E&W Win. | -1.276 | -1.2901 | -1.203 | -1.3287 | -1.4313 | -1.2918 | -1.4313 | -1.203 | -1.3035 | 17.51% | -1.274 | ○
930-630 Mass w/ E&W Shade | -0.913 | -0.94541 | -0.879 | -0.91693 | -0.9415 | -0.90111 | -0.94541 | -0.879 | -0.91616 | 7.249% | -0.91 | ○
940-640 Mass, w/ Htg. Setback | -3.191 | -3.2473 | -2.894 | -3.3387 | -3.465 | -3.2738 | -3.465 | -2.894 | -3.235 | 17.65% | -3.034 | ○
950-650 Mass, w/ Night Vent | -4.043 | -4.0559 | -3.568 | -4.1099 | -4.2891 | -3.9907 | -4.2891 | -3.568 | -4.0094 | 17.99% | -3.8775 | ○
980-680 Mass, w/ Insulation 20/27 | -2.437 | -2.4346 | -2.174 | -2.7321 | -2.7549 | -2.7912 | -2.7912 | -2.174 | -2.554 | 24.17% | -2.6104 | ○
985-685 Mass, w/ 20/20 Tstat | -1.857 | -2.6256 | -2.358 | -2.7596 | -2.8721 | -2.7378 | -2.8721 | -1.857 | -2.535 | 40.04% | -2.481 | ○
995-695 Mass, w/ Insulation 20/20 | -1.273 | -1.772 | -1.615 | -1.9687 | -2.0002 | -1.9753 | -2.0002 | -1.273 | -1.7674 | 41.15% | -1.8714 | ○
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
800-430 Mass, w/ High Cond. Wall | -0.343 | -0.47625 | -0.496 | -0.3926 | -0.445 | -0.44187 | -0.496 | -0.343 | -0.43245 | 35.38% | -0.437 | ○
900-800 Himass, S. Win. | -0.406 | -0.33425 | -0.411 | -0.23616 | -0.207 | -0.18847 | -0.411 | -0.18847 | -0.29715 | 74.89% | -0.174 | 6.501%
900-810 Himass, Int. Sol. Abs. |  | -0.056746 | -0.059 | -0.061545 | -0.062 | -0.066177 | -0.066177 | -0.056746 | -0.061094 | 15.44% | -0.055 | 18.51%
910-610 Mass, w/ S. Shade | -0.405 | -0.55173 | -0.565 | -0.49292 | -0.549 | -0.56031 | -0.565 | -0.405 | -0.52066 | 30.73% | -0.51 | ○
920-620 Mass, w/ E&W Win. | -0.25 | -0.52543 | -0.555 | -0.45894 | -0.547 | -0.52032 | -0.555 | -0.25 | -0.47612 | 64.06% | -0.5 | ○
930-630 Mass w/ E&W Shade | -0.284 | -0.5024 | -0.523 | -0.42166 | -0.494 | -0.48714 | -0.523 | -0.284 | -0.45203 | 52.87% | -0.473 | ○
940-640 Mass, w/ Htg. Setback | -0.751 | -1.1705 | -0.999 | -1.4158 | -0.979 | -0.63372 | -1.4158 | -0.63372 | -0.9915 | 78.87% | -0.821 | ○
980-680 Mass, w/ Insulation 20/27 | -0.433 | -0.52385 | -0.429 | -0.51458 | -0.549 | -0.52258 | -0.549 | -0.429 | -0.49534 | 24.23% | -0.441 | ○ | -1 | -0.52385 | -0.433 | -0.49534 | 0.11946 | -17 | -1
985-685 Mass, w/ 20/20 Tstat | -0.415 | -0.57969 | -0.596 | -0.52772 | -0.605 | -0.58899 | -0.605 | -0.415 | -0.55207 | 34.42% | -0.548 | ○ | 5 | -0.57969 | -0.58899 | -0.55207 | 0.019048 | -22 | -18
995-695 Mass, w/ Insulation 20/20 | -0.427 | -0.42577 | -0.393 | -0.44966 | -0.465 | -0.45573 | -0.465 | -0.393 | -0.43603 | 16.51% | -0.396 | ○ | -2 | -0.42577 | -0.427 | -0.43603 | 0.046956 | -17 | -1
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
800-430 Mass, w/ High Cond. Wall | -0.881 | -0.73794 | -0.683 | -0.88353 | -0.822 | -0.76849 | -0.88353 | -0.683 | -0.79599 | 25.19% | -0.661 | -2.764%
900-800 Himass, S. Win. | 1.753 | 2.2746 | 1.399 | 1.9946 | 1.844 | 2.0045 | 1.399 | 2.2746 | 1.8783 | 46.62% | 1.802 | ○
900-810 Himass, Int. Sol. Abs. |  | 0.96595 | 0.616 | 0.77023 | 0.717 | 0.8272 | 0.616 | 0.96595 | 0.77927 | 44.91% | 0.585 | -8.858%
910-610 Mass, w/ S. Shade | -2.973 | -3.7101 | -3.228 | -3.9124 | -3.722 | -3.7868 | -3.9124 | -2.973 | -3.5554 | 26.42% | -3.208 | ○
920-620 Mass, w/ E&W Win. | -1.223 | -1.4361 | -1.245 | -1.5371 | -1.523 | -1.4341 | -1.5371 | -1.223 | -1.3997 | 22.44% | -1.327 | ○
930-630 Mass w/ E&W Shade | -1.069 | -1.3365 | -1.191 | -1.4307 | -1.477 | -1.3363 | -1.477 | -1.069 | -1.3067 | 31.22% | -1.195 | ○
940-640 Mass, w/ Htg. Setback | -2.492 | -3.0526 | -2.809 | -3.2574 | -3.236 | -3.0295 | -3.2574 | -2.492 | -2.9794 | 25.69% | -2.677 | ○
950-650 Mass, w/ Night Vent | -3.282 | -3.9262 | -2.991 | -3.7506 | -3.759 | -3.5611 | -3.9262 | -2.991 | -3.545 | 26.38% | -3.104 | ○
980-680 Mass, w/ Insulation 20/27 | -2.377 | -3.3833 | -2.931 | -3.3201 | -3.335 | -3.244 | -3.3833 | -2.377 | -3.0984 | 32.48% | -2.871 | ○ | 0 | -2.831 | -3.3833 | -3.0984 | 0.020291
985-685 Mass, w/ 20/20 Tstat | -2.341 | -2.9342 | -2.863 | -3.192 | -3.198 | -2.9827 | -3.198 | -2.341 | -2.9185 | 29.36% | -2.772 | ○ | 0 | -2.863 | -2.9342 | -2.9185 | 0.10458
995-695 Mass, w/ Insulation 20/20 | -2.103 | -3.3169 | -3.04 | -3.1569 | -3.285 | -3.0602 | -3.3169 | -2.103 | -2.9937 | 40.55% | -2.975 | ○ | 1 | -2.917 | -3.3169 | -2.9937 | 0.040497
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 6
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-11. Annual Transmissivity Coefficient of Windows
(ANNUAL UNSHADED TRANSMITTED SOLAR RADIATION)/(ANNUAL UNSHADED INCIDENT SOLAR RADIATION)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
600 South | 0.5912 | 0.62686 | 0.62378 | 0.58667 | 0.59708 | 0.59426 | 0.58667 | 0.62686 | 0.60331 | 6.661% | 0.58125 | -13.49%
620 West | 0.5998 |  | 0.62866 | 0.6007 | 0.61578 | 0.64014 | 0.5998 | 0.64014 | 0.61702 | 6.538% | 0.65551 | 38.12%
660 South, Low-E | 0.32228 | 0.38067 | 0.39243 | 0.31813 | 0.32477 | 0.324 | 0.31813 | 0.39243 | 0.34371 | 21.61% | 0.32117 | ○
670 South, Single-Pane | 0.74766 | 0.7501 | 0.77043 | 0.74733 | 0.75442 | 0.75076 | 0.74733 | 0.77043 | 0.75345 | 3.067% | 0.75089 | ○
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-12. Annual Shading Coefficient of Window Shading Devices: Overhangs & Fins
(1-(ANNUAL SHADED TRANSMITTED SOLAR RADIATION)/(ANNUAL UNSHADED TRANSMITTED SOLAR RADIATION))
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
610/600 South | 0.21829 | 0.19413 | 0.17602 | 0.19637 | 0.2243 | 0.19545 | 0.17602 | 0.2243 | 0.20076 | 24.05% | 0.17525 | -1.587%
630/620 West | 0.26756 |  | 0.29895 | 0.27827 | 0.34164 | 0.28575 | 0.26756 | 0.34164 | 0.29443 | 25.16% | 0.26912 | ○
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-13. Case 600 Annual Incident Solar Radiation (kWh/m2)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
Horizontal | 1670 | 1662.5278 | 1667.158 | 1664.3425 | 1665.18 | 1668.98 | 1662.5278 | 1670 | 1666.3647 | 0.4484% | 1663.67 | ○ | 0
North | 453 | 399.0475 | 477.31 | 438.241 | 432.12 | 440.165 | 399.0475 | 477.31 | 439.9806 | 17.79% | 432.25 | ○ | 1
East | 1061 | 1026.9874 | 1016.676 | 1062.1572 | 1054.24 | 1067.94 | 1016.676 | 1067.94 | 1048.1668 | 4.891% | 1061 | ○ | 2
South | 1387 | 1316.9162 | 1290.593 | 1370.4819 | 1363.1 | 1384.23 | 1290.593 | 1387 | 1352.0535 | 7.13% | 1381.75 | ○ | 3
West | 997 | 903.0665 | 905.722 | 967.278 | 961.18 | 974.473 | 903.0665 | 997 | 951.4533 | 9.873% | 968.92 | ○ | 4
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-14. Annual Transmitted Solar Radiation - Unshaded (kWh/m2)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
600 South | 820 | 825.5194 | 805.046 | 804.0205 | 813.88 | 822.589 | 804.0205 | 825.5194 | 815.1758 | 2.637% | 803.14 | -4.096%
620 West | 598 |  | 569.394 | 581.0395 | 591.88 | 623.797 | 569.394 | 623.797 | 592.8221 | 9.177% | 635.14 | 20.85%
660 South | 447 | 501.3136 | 506.461 | 435.995 | 442.7 | 448.493 | 435.995 | 506.461 | 463.6604 | 15.2% | 443.78 | ○
670 South | 1037 | 987.8182 | 994.318 | 1024.2026 | 1028.35 | 1039.23 | 987.8182 | 1039.23 | 1018.4865 | 5.048% | 1037.54 | ○
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-15. Annual Transmitted Solar Radiation - Shaded (kWh/m2)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
610 South | 641 | 665.2609 | 663.345 | 646.1319 | 631.33 | 661.81 | 631.33 | 665.2609 | 651.4796 | 5.208% | 662.39 | ○
630 West | 438 |  | 399.173 | 419.3545 | 389.67 | 445.549 | 389.67 | 445.549 | 418.3493 | 13.36% | 464.21 | 33.4%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 7
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-16. Sky Temperature Output, Case 600
MAXIMUM ANNUAL HOURLY INTEGRATED SKY TEMPERATURE
Simulation Model: | BSIMAC |  |  |  | CSE |  |  |  | DeST |  |  |  | EnergyPlus |  |  |  | ESP-r |  |  |  | TRNSYS |  |  |  | TestSpec-Alt |  |  |  | Example Result Statistics |  |  |  |  | Tested Prg
[25 empty] | Alternative Values |  |  |  | Min | Max | Mean | (Max-Min)/
Case | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | T (°C) | T (°C) | Mean** (%) | T (°C) | Mo. | Day | Hr
Average Annual Hourly Integrated |  |  |  |  | -3.9307 |  |  |  | -5.9 |  |  |  | -2.0216 |  |  |  | -5.17 |  |  |  | -5.0587 |  |  |  | -5.9 |  |  |  | -5.9 | -2.0216 | -4.6635 | 83.16% | -5.27 |  |  |  | 0 | 0
Minimum Annual Hourly Integrated |  |  |  |  | -46.2246 | Dec | 31 | 24 | -46.85 | Dec | 31 | 23 | -37.9798 | Dec | 31 | 24 | -46.9 | Dec | 31 | 23 | -46.1617 | Dec | 31 | 24 | -46.85 |  |  |  | -46.9 | -37.9798 | -45.161 | 19.75% | -46.97 | Dec | 31 | 23
Maximum Annual Hourly Integrated |  |  |  |  | 30.0812 | Jun | 13 | 15 | 24.62 | Aug | 4 | 15 | 24.7268 | Aug | 4 | 16 | 26.7 | Aug | 4 | 15 | 26.0293 | Jun | 13 | 18 | 24.62 |  |  |  | 24.62 | 30.0812 | 26.1296 | 20.9% | 27.28 | Aug | 5 | 11
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables M1
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-M1. Monthly Heating Loads (kWh) | [12 empty] | Annual Sums Check (kWh)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0
[7 empty] | Min | Max | Mean | (Max-Min)/
Case 600 | [9 empty] | Mean** (%) |  |  | 600 Heating
Jan | 663.99 | 655.585 | 672.684 | 711.8797 | 732 | 734.943 | 655.585 | 734.943 | 695.1803 | 11.42% | 719.33 | 0 | 4049.581 | 3992.755 | 4048.646 | 4324.3743 | 4364 | 4503.5533 | #REF! | #REF!
Feb | 653.26 | 626.2627 | 635.299 | 682.632 | 682 | 702.079 | 626.2627 | 702.079 | 663.5888 | 11.43% | 687.11 | 1
Mar | 433.508 | 435.7419 | 450.494 | 472.2167 | 481 | 495.001 | 433.508 | 495.001 | 461.3269 | 13.33% | 493.74 | 2
Apr | 511.036 | 456.9543 | 447.957 | 510.1244 | 479 | 517.287 | 447.957 | 517.287 | 487.0598 | 14.23% | 516.41 | 3
May | 112.769 | 127.7958 | 128 | 136.8192 | 139 | 150.732 | 112.769 | 150.732 | 132.5193 | 28.65% | 156.11 | 4
Jun | 2.735 | 11.6999 | 11.218 | 10.0812 | 14 | 15.9512 | 2.735 | 15.9512 | 10.9476 | 120.7% | 18.4 | 5
Jul | 4.839 | 11.5431 | 10.105 | 12.0182 | 14 | 16.7263 | 4.839 | 16.7263 | 11.5386 | 103% | 18.44 | 6
Aug | 1.368 | 6.9186 | 8.376 | 6.5877 | 9 | 9.6039 | 1.368 | 9.6039 | 6.9757 | 118.1% | 11.83 | 7
Sep | 51.756 | 74.3067 | 76.741 | 73.317 | 81 | 84.8239 | 51.756 | 84.8239 | 73.6574 | 44.89% | 89.27 | 8
Oct | 316.952 | 328.4088 | 324.148 | 347.7084 | 354 | 367.051 | 316.952 | 367.051 | 339.7114 | 14.75% | 363.1 | 9
Nov | 598.664 | 575.553 | 585.805 | 625.2596 | 629 | 645.809 | 575.553 | 645.809 | 610.0151 | 11.52% | 632.65 | 10
Dec | 698.704 | 681.9851 | 697.819 | 735.7303 | 750 | 763.546 | 681.9851 | 763.546 | 721.2974 | 11.31% | 749.73 | 11
Case 900 | [12 empty] | 900 Heating
Jan | 277.8 | 206.1043 | 275.307 | 255.8355 | 266 | 291.936 | 206.1043 | 291.936 | 262.1638 | 32.74% | 282.23 |  | 1726 | 1378.8913 | 1590.894 | 1663.6867 | 1585 | 1814.0316 | #REF! | #REF!
Feb | 307.4 | 243.2297 | 292.916 | 294.1814 | 283 | 322.141 | 243.2297 | 322.141 | 290.478 | 27.17% | 312.77
Mar | 134.4 | 102.4399 | 119.976 | 125.5424 | 115 | 143.84 | 102.4399 | 143.84 | 123.5331 | 33.51% | 140.44
Apr | 275.7 | 222.3692 | 214.166 | 268.6543 | 228 | 275.466 | 214.166 | 275.7 | 247.3926 | 24.87% | 271.95
May | 20.1 | 33.3469 | 26.771 | 33.4139 | 29 | 37.5028 | 20.1 | 37.5028 | 30.0224 | 57.97% | 35.54
Jun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
Jul | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
Aug | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
Sep | 2.1 | 0 | 0 | 0.11241 | 0 | 0.53697 | 0 | 2.1 | 0.45823 | 458.3% | 0.3
Oct | 80.5 | 65.0694 | 63.591 | 81.0905 | 70 | 85.0098 | 63.591 | 85.0098 | 74.2101 | 28.86% | 81.19
Nov | 298.2 | 251.5988 | 283.888 | 296.9874 | 286 | 318.242 | 251.5988 | 318.242 | 289.1527 | 23.05% | 308.36
Dec | 329.8 | 254.733 | 314.279 | 307.8688 | 308 | 339.357 | 254.733 | 339.357 | 309.0063 | 27.39% | 332.3
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-M2. Monthly Sensible Cooling Loads (kWh)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
[7 empty] | Min | Max | Mean | (Max-Min)/
Case 600 | [9 empty] | Mean** (%) |  |  | 600 Cooling
Jan | 475.4 | 554.0235 | 417.93 | 521.798 | 523 | 495.012 | 417.93 | 554.0235 | 497.8606 | 27.34% | 478.98 | 0 | 5822 | 5913.1242 | 5432.086 | 6027.0394 | 6161 | 5779.524 | #REF! | #REF!
Feb | 349.2 | 394.2972 | 315.415 | 387.4981 | 398 | 367.404 | 315.415 | 398 | 368.6357 | 22.4% | 360.93 | 1
Mar | 450.3 | 474.3508 | 410.736 | 484.3611 | 489 | 457.384 | 410.736 | 489 | 461.022 | 16.98% | 460.76 | 2
Apr | 218.7 | 220.1356 | 230.168 | 240.4611 | 263 | 235.357 | 218.7 | 263 | 234.6369 | 18.88% | 240.77 | 3
May | 342.7 | 321.1602 | 338.582 | 339.9139 | 364 | 325.154 | 321.1602 | 364 | 338.585 | 12.65% | 329.98 | 4
Jun | 578.3 | 497.4498 | 526.439 | 539.605 | 550 | 516.057 | 497.4498 | 578.3 | 534.6418 | 15.12% | 516.12 | 5
Jul | 568.4 | 505.8671 | 525.149 | 536.3834 | 556 | 514.389 | 505.8671 | 568.4 | 534.3648 | 11.7% | 517.58 | 6
Aug | 658.2 | 606.5032 | 621.101 | 648.5013 | 674 | 634.136 | 606.5032 | 674 | 640.4069 | 10.54% | 645.94 | 7
Sep | 724.8 | 705.1929 | 672.084 | 733.708 | 743 | 710.474 | 672.084 | 743 | 714.8765 | 9.92% | 727.97 | 8
Oct | 628.4 | 676.133 | 611.126 | 675.2687 | 681 | 649.483 | 611.126 | 681 | 653.5685 | 10.69% | 654.28 | 9
Nov | 394.3 | 454.7409 | 377.147 | 437.6814 | 444 | 418.571 | 377.147 | 454.7409 | 421.0734 | 18.43% | 413.33 | 10
Dec | 433.3 | 503.27 | 386.209 | 481.8594 | 476 | 456.103 | 386.209 | 503.27 | 456.1236 | 25.66% | 443.2 | 11
Case 900 | [12 empty] | 900 Cooling
Jan | 73.3141 | 67.8041 | 33.493 | 53.2805 | 42 | 44.635 | 33.493 | 73.3141 | 52.4211 | 75.96% | 53.11 |  | 2714 | 2463.8258 | 2382.684 | 2488.7414 | 2485 | 2267.1274 | #REF! | #REF!
Feb | 24.0087 | 15.1117 | 4.724 | 12.3391 | 11 | 9.2434 | 4.724 | 24.0087 | 12.7378 | 151.4% | 13.47
Mar | 86.3882 | 68.5488 | 40.898 | 65.3862 | 56 | 50.5508 | 40.898 | 86.3882 | 61.2953 | 74.21% | 65.77
Apr | 29.344 | 12.3134 | 18.267 | 18.4694 | 22 | 16.0525 | 12.3134 | 29.344 | 19.4077 | 87.75% | 21.99
May | 131.0941 | 117.8126 | 128.592 | 114.4874 | 125 | 98.3549 | 98.3549 | 131.0941 | 119.2235 | 27.46% | 107.69
Jun | 447.4956 | 372.2992 | 408.473 | 401.3344 | 404 | 365.819 | 365.819 | 447.4956 | 399.9035 | 20.42% | 378.33
Jul | 440.8962 | 380.4363 | 408.145 | 398.7064 | 410 | 365.513 | 365.513 | 440.8962 | 400.6161 | 18.82% | 382.01
Aug | 532.6434 | 485.6761 | 510.152 | 510.3174 | 531 | 487.566 | 485.6761 | 532.6434 | 509.5592 | 9.217% | 517.28
Sep | 517.8661 | 484.0294 | 466.106 | 492.837 | 492 | 458.859 | 458.859 | 517.8661 | 485.2829 | 12.16% | 500.2
Oct | 296.188 | 305.5693 | 269.566 | 292.6655 | 281 | 260.853 | 260.853 | 305.5693 | 284.307 | 15.73% | 292.83
Nov | 72.6701 | 80.4854 | 56.214 | 67.9828 | 63 | 60.1796 | 56.214 | 80.4854 | 66.7553 | 36.36% | 70.48
Dec | 62.0916 | 73.7394 | 38.054 | 60.9353 | 48 | 49.5012 | 38.054 | 73.7394 | 55.3869 | 64.43% | 57.43
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables M2
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-M3. Monthly Hourly Integrated Peak Heating Loads | [26 empty] | Annual Peaks Check (kWh)
Simulation Model: | BSIMAC |  |  | CSE |  |  | DeST |  |  | EnergyPlus |  |  | ESP-r |  |  | TRNSYS |  |  | Example Result Statistics |  |  |  |  | Tested Prg |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0
[19 empty] | Min | Max | Mean | (Max-Min)/
Case 600 | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | kW | kW | Mean** (%) | kW | Day | Hr |  | 600 Heating
Jan | 3.1 | 29 | 7 | 3.0202 | 1 | 1 | 3.036 | 1 | 0 | 2.9776 | 1 | 3 | 3.23 | 1 | 1 | 3.3589 | 1 | 1 | 2.9776 | 3.3589 | 3.1204 | 12.22% | 2.999 | 1 | 4 | 0 | 3.255 | 3.0202 | 3.036 | 3.2044 | 3.23 | 3.3589 | #REF! | #REF!
Feb | 3.041 | 9 | 7 | 2.8997 | 9 | 6 | 2.922 | 9 | 5 | 3.0666 | 9 | 6 | 3.14 | 9 | 6 | 3.2252 | 9 | 6 | 2.8997 | 3.2252 | 3.0491 | 10.68% | 3.13 | 9 | 6 | 1
Mar | 2.275 | 2 | 7 | 2.0344 | 17 | 6 | 2.065 | 17 | 5 | 2.1146 | 17 | 6 | 2.23 | 17 | 6 | 2.287 | 17 | 6 | 2.0344 | 2.287 | 2.1677 | 11.65% | 2.274 | 17 | 6 | 2
Apr | 2.446 | 3 | 6 | 2.2073 | 11 | 6 | 2.238 | 11 | 5 | 2.3223 | 11 | 5 | 2.38 | 11 | 6 | 2.4572 | 11 | 6 | 2.2073 | 2.4572 | 2.3418 | 10.67% | 2.408 | 11 | 5 | 3
May | 1.645 | 3 | 5 | 1.5922 | 1 | 5 | 1.569 | 1 | 4 | 1.6241 | 1 | 5 | 1.75 | 1 | 5 | 1.778 | 1 | 5 | 1.569 | 1.778 | 1.6597 | 12.59% | 1.746 | 1 | 4 | 4
Jun | 0.805 | 9 | 5 | 0.77848 | 9 | 5 | 0.748 | 9 | 4 | 0.73243 | 9 | 5 | 0.76 | 10 | 5 | 0.8526 | 9 | 5 | 0.73243 | 0.8526 | 0.77942 | 15.42% | 0.905 | 9 | 5 | 5
Jul | 0.599 | 25 | 6 | 0.53975 | 26 | 5 | 0.512 | 26 | 4 | 0.51445 | 26 | 5 | 0.57 | 26 | 5 | 0.61893 | 26 | 5 | 0.512 | 0.61893 | 0.55902 | 19.13% | 0.673 | 26 | 5 | 6
Aug | 0.572 | 10 | 7 | 0.55338 | 17 | 6 | 0.532 | 17 | 5 | 0.47852 | 17 | 6 | 0.56 | 17 | 6 | 0.59085 | 17 | 6 | 0.47852 | 0.59085 | 0.54779 | 20.5% | 0.624 | 17 | 5 | 7
Sep | 1.229 | 28 | 24 | 1.1204 | 29 | 1 | 1.114 | 29 | 2 | 1.1295 | 28 | 24 | 1.19 | 29 | 1 | 1.2116 | 28 | 24 | 1.114 | 1.229 | 1.1657 | 9.865% | 1.232 | 28 | 24 | 8
Oct | 1.702 | 6 | 7 | 1.6237 | 15 | 6 | 1.619 | 9 | 5 | 1.682 | 15 | 5 | 1.77 | 9 | 6 | 1.8132 | 15 | 6 | 1.619 | 1.8132 | 1.7017 | 11.41% | 1.772 | 9 | 6 | 9
Nov | 3.255 | 26 | 8 | 2.8502 | 26 | 8 | 2.931 | 26 | 7 | 3.1061 | 26 | 7 | 3.11 | 26 | 7 | 3.2066 | 26 | 8 | 2.8502 | 3.255 | 3.0765 | 13.16% | 3.117 | 26 | 7 | 10
Dec | 3.171 | 31 | 24 | 2.9413 | 31 | 24 | 2.972 | 31 | 23 | 3.2044 | 31 | 24 | 3.17 | 31 | 24 | 3.2781 | 31 | 24 | 2.9413 | 3.2781 | 3.1228 | 10.79% | 3.198 | 31 | 24 | 11
Case 900 | [26 empty] | 900 Heating
Jan | 2.322 | 7 | 7 | 2.0774 | 1 | 5 | 2.178 | 1 | 4 | 1.9028 | 29 | 7 | 2.2 | 1 | 5 | 2.3786 | 1 | 5 | 1.9028 | 2.3786 | 2.1765 | 21.86% | 1.968 | 1 | 7 | 0 | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.63 | 2.7785 | #REF! | #REF!
Feb | 2.551 | 8 | 24 | 2.4434 | 9 | 6 | 2.453 | 9 | 5 | 2.6875 | 9 | 6 | 2.63 | 9 | 7 | 2.7785 | 9 | 7 | 2.4434 | 2.7785 | 2.5906 | 12.93% | 2.672 | 9 | 6 | 1
Mar | 1.774 | 16 | 7 | 1.6129 | 17 | 6 | 1.646 | 17 | 5 | 1.7443 | 17 | 6 | 1.76 | 17 | 7 | 1.8582 | 17 | 6 | 1.6129 | 1.8582 | 1.7326 | 14.16% | 1.847 | 17 | 6 | 2
Apr | 1.997 | 2 | 7 | 1.7706 | 3 | 4 | 1.725 | 3 | 3 | 2.0036 | 3 | 4 | 1.93 | 3 | 4 | 2.0359 | 3 | 4 | 1.725 | 2.0359 | 1.9104 | 16.28% | 1.981 | 3 | 3 | 3
May | 1.295 | 4 | 6 | 1.1425 | 1 | 5 | 1.124 | 1 | 5 | 1.2682 | 1 | 5 | 1.23 | 1 | 5 | 1.3242 | 1 | 5 | 1.124 | 1.3242 | 1.2307 | 16.27% | 1.315 | 1 | 5 | 4
Jun | 0 |  |  | 0 | 1 | 1 |  |  |  | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 31 | 0 | 0 | 0 | 0 | ---- | 0 |  |  | 5
Jul | 0 |  |  | 0 | 1 | 1 |  |  |  | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 31 | 0 | 0 | 0 | 0 | ---- | 0 |  |  | 6
Aug | 0 |  |  | 0 | 1 | 1 |  |  |  | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 31 | 0 | 0 | 0 | 0 | ---- | 0 |  |  | 7
Sep | 0.113 | 28 | 6 | 0 | 1 | 1 |  |  |  | 0.064157 | 29 | 7 | 0 | 1 | 1 | 0.19442 | 29 | 7 | 0 | 0.19442 | 0.074315 | 261.6% | 0.152 | 29 | 7 | 8
Oct | 1.201 | 6 | 7 | 1.1882 | 7 | 7 | 1.158 | 7 | 6 | 1.3258 | 7 | 7 | 1.21 | 7 | 7 | 1.3311 | 7 | 7 | 1.158 | 1.3311 | 1.2357 | 14.01% | 1.312 | 7 | 7 | 9
Nov | 2.427 | 1 | 7 | 2.0863 | 26 | 8 | 2.201 | 26 | 7 | 2.3161 | 26 | 7 | 2.28 | 26 | 8 | 2.4629 | 26 | 8 | 2.0863 | 2.4629 | 2.2956 | 16.4% | 2.394 | 26 | 8 | 10
Dec | 2.12 | 31 | 8 | 1.9268 | 31 | 8 | 1.981 | 9 | 6 | 2.1749 | 31 | 7 | 2.04 | 9 | 7 | 2.1801 | 9 | 7 | 1.9268 | 2.1801 | 2.0705 | 12.24% | 2.136 | 31 | 24 | 11
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-M4. Monthly Hourly Integrated Peak Sensible Cooling Loads
Simulation Model: | BSIMAC |  |  | CSE |  |  | DeST |  |  | EnergyPlus |  |  | ESP-r |  |  | TRNSYS |  |  | Example Result Statistics |  |  |  |  | Tested Prg
[19 empty] | Min | Max | Mean | (Max-Min)/
Case 600 | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | kW | kW | Mean** (%) | kW | Day | Hr |  | 600 Cooling
Jan | 5.65 | 22 | 15 | 6.481 | 22 | 14 | 5.422 | 22 | 14 | 6.3516 | 22 | 14 | 6.19 | 22 | 14 | 6.0457 | 22 | 14 | 5.422 | 6.481 | 6.0234 | 17.58% | 5.523 | 22 | 14 | 0 | 5.65 | 6.481 | 5.422 | 6.3516 | 6.19 | 6.0457 | #REF! | #REF!
Feb | 4.9211 | 15 | 15 | 5.3928 | 15 | 14 | 4.444 | 15 | 14 | 5.5373 | 2 | 14 | 5.42 | 2 | 14 | 5.1553 | 2 | 14 | 4.444 | 5.5373 | 5.1451 | 21.25% | 4.798 | 15 | 14 | 1
Mar | 4.4579 | 24 | 14 | 5.1483 | 24 | 13 | 4.252 | 9 | 14 | 5.0085 | 9 | 14 | 5.04 | 9 | 14 | 4.7399 | 9 | 14 | 4.252 | 5.1483 | 4.7744 | 18.77% | 4.402 | 24 | 14 | 2
Apr | 3.4735 | 12 | 14 | 4.0151 | 27 | 14 | 3.6 | 7 | 14 | 3.9307 | 12 | 14 | 4.04 | 12 | 14 | 3.8027 | 12 | 14 | 3.4735 | 4.04 | 3.8103 | 14.87% | 3.65 | 12 | 14 | 3
May | 2.7741 | 10 | 14 | 3.0796 | 21 | 14 | 2.894 | 10 | 14 | 3.0864 | 10 | 13 | 3.1 | 10 | 14 | 3.0405 | 21 | 14 | 2.7741 | 3.1 | 2.9958 | 10.88% | 2.899 | 21 | 14 | 4
Jun | 3.2526 | 26 | 15 | 3.2488 | 13 | 13 | 3.067 | 14 | 14 | 3.4487 | 13 | 13 | 3.43 | 13 | 14 | 3.3792 | 13 | 13 | 3.067 | 3.4487 | 3.3044 | 11.55% | 3.22 | 13 | 13 | 5
Jul | 3.3187 | 17 | 14 | 3.2903 | 17 | 14 | 3.155 | 29 | 13 | 3.6284 | 17 | 14 | 3.64 | 17 | 14 | 3.4967 | 17 | 14 | 3.155 | 3.64 | 3.4215 | 14.17% | 3.409 | 29 | 14 | 6
Aug | 4.1922 | 26 | 14 | 4.1195 | 8 | 14 | 4.038 | 29 | 13 | 4.672 | 26 | 14 | 4.7 | 29 | 14 | 4.6505 | 27 | 13 | 4.038 | 4.7 | 4.3954 | 15.06% | 4.414 | 27 | 13 | 7
Sep | 5.086 | 30 | 14 | 5.4503 | 2 | 14 | 4.911 | 30 | 13 | 5.7148 | 30 | 13 | 5.58 | 30 | 14 | 5.4199 | 30 | 14 | 4.911 | 5.7148 | 5.3603 | 15% | 5.18 | 30 | 14 | 8
Oct | 5.5767 | 18 | 14 | 6.2702 | 1 | 13 | 5.278 | 10 | 13 | 6.2221 | 18 | 14 | 6.07 | 18 | 14 | 5.9226 | 18 | 14 | 5.278 | 6.2702 | 5.8899 | 16.85% | 5.609 | 18 | 14 | 9
Nov | 5.4759 | 28 | 14 | 6.149 | 28 | 13 | 5.229 | 29 | 13 | 6.194 | 28 | 13 | 6.03 | 28 | 14 | 5.824 | 28 | 14 | 5.229 | 6.194 | 5.817 | 16.59% | 5.407 | 28 | 14 | 10
Dec | 5.537 | 1 | 14 | 6.45 | 1 | 14 | 5.294 | 1 | 13 | 6.251 | 1 | 14 | 6.12 | 1 | 14 | 5.9425 | 1 | 14 | 5.294 | 6.45 | 5.9324 | 19.49% | 5.45 | 1 | 14 | 11
Case 900 | [26 empty] | 900 Cooling
Jan | 1.982 | 22 | 16 | 2.2416 | 22 | 15 | 1.637 | 22 | 15 | 2.0779 | 22 | 15 | 1.81 | 22 | 16 | 1.8776 | 22 | 15 | 1.637 | 2.2416 | 1.9377 | 31.2% | 1.932 | 22 | 15 | 0 | 3.039 | 3.3764 | 2.556 | 3.0404 | 2.9 | 2.9401 | #REF! | #REF!
Feb | 1.096 | 15 | 16 | 0.99617 | 15 | 15 | 0.588 | 15 | 15 | 0.97943 | 15 | 15 | 0.85 | 15 | 16 | 0.82938 | 15 | 15 | 0.588 | 1.096 | 0.88983 | 57.09% | 1.03 | 15 | 15 | 1
Mar | 1.508 | 10 | 15 | 1.4341 | 24 | 15 | 1.143 | 10 | 14 | 1.4931 | 11 | 14 | 1.27 | 10 | 15 | 1.4258 | 11 | 14 | 1.143 | 1.508 | 1.379 | 26.47% | 1.637 | 11 | 14 | 2
Apr | 1.093 | 7 | 15 | 0.63116 | 19 | 14 | 1.032 | 8 | 14 | 0.95262 | 7 | 15 | 0.95 | 8 | 15 | 0.83719 | 8 | 15 | 0.63116 | 1.093 | 0.916 | 50.42% | 1.073 | 7 | 15 | 3
May | 1.555 | 11 | 15 | 1.4272 | 21 | 14 | 1.446 | 11 | 14 | 1.5339 | 11 | 14 | 1.46 | 11 | 15 | 1.4645 | 11 | 14 | 1.4272 | 1.555 | 1.4811 | 8.626% | 1.532 | 11 | 14 | 4
Jun | 2.101 | 26 | 15 | 1.8967 | 14 | 14 | 1.873 | 14 | 14 | 1.9656 | 14 | 14 | 1.89 | 14 | 15 | 1.9742 | 14 | 14 | 1.873 | 2.101 | 1.9501 | 11.69% | 1.912 | 14 | 14 | 5
Jul | 2.14 | 17 | 15 | 1.943 | 17 | 14 | 1.83 | 17 | 14 | 2.0681 | 17 | 15 | 1.97 | 17 | 15 | 1.975 | 17 | 15 | 1.83 | 2.14 | 1.9877 | 15.6% | 2.022 | 17 | 14 | 6
Aug | 2.632 | 26 | 15 | 2.4852 | 5 | 14 | 2.212 | 29 | 14 | 2.5258 | 29 | 15 | 2.51 | 29 | 15 | 2.5337 | 29 | 15 | 2.212 | 2.632 | 2.4831 | 16.91% | 2.484 | 29 | 14 | 7
Sep | 2.961 | 30 | 15 | 3.1368 | 4 | 14 | 2.556 | 11 | 14 | 2.9888 | 11 | 15 | 2.81 | 11 | 15 | 2.8712 | 11 | 15 | 2.556 | 3.1368 | 2.8873 | 20.11% | 2.818 | 11 | 14 | 8
Oct | 3.039 | 1 | 15 | 3.3764 | 1 | 14 | 2.549 | 12 | 14 | 3.0404 | 1 | 14 | 2.9 | 12 | 15 | 2.9401 | 1 | 14 | 2.549 | 3.3764 | 2.9742 | 27.82% | 2.785 | 1 | 14 | 9
Nov | 1.982 | 6 | 15 | 2.2328 | 20 | 15 | 1.683 | 20 | 14 | 2.0018 | 20 | 15 | 1.94 | 20 | 15 | 1.9406 | 22 | 14 | 1.683 | 2.2328 | 1.9634 | 28% | 1.978 | 22 | 14 | 10
Dec | 2.069 | 1 | 15 | 2.1054 | 1 | 15 | 1.595 | 2 | 14 | 1.9682 | 2 | 15 | 1.67 | 2 | 15 | 1.6903 | 2 | 15 | 1.595 | 2.1054 | 1.8497 | 27.59% | 1.781 | 2 | 15 | 11
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables M3
ASHRAE Standard 140-2023, Informative Annex B8, Section B8.1
Example Results for Section 7 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-M5. Monthly Load 600-900 Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Month | [6 empty] | Min | Max | Mean | Mean** (%)
Jan | 386.19 | 449.4807 | 397.377 | 456.0442 | 466 | 443.007 | 386.19 | 466 | 433.0165 | 18.43% | 437.1
Feb | 345.86 | 383.033 | 342.383 | 388.4505 | 399 | 379.938 | 342.383 | 399 | 373.1108 | 15.17% | 374.34
Mar | 299.108 | 333.302 | 330.518 | 346.6743 | 366 | 351.161 | 299.108 | 366 | 337.7939 | 19.8% | 353.3
Apr | 235.336 | 234.5851 | 233.791 | 241.4701 | 251 | 241.821 | 233.791 | 251 | 239.6672 | 7.18% | 244.46
May | 92.669 | 94.449 | 101.229 | 103.4052 | 110 | 113.2292 | 92.669 | 113.2292 | 102.4969 | 20.06% | 120.57
Jun | 2.735 | 11.6999 | 11.218 | 10.0812 | 14 | 15.9512 | 2.735 | 15.9512 | 10.9476 | 120.7% | 18.4
Jul | 4.839 | 11.5431 | 10.105 | 12.0182 | 14 | 16.7263 | 4.839 | 16.7263 | 11.5386 | 103% | 18.44
Aug | 1.368 | 6.9186 | 8.376 | 6.5877 | 9 | 9.6039 | 1.368 | 9.6039 | 6.9757 | 118.1% | 11.83
Sep | 49.656 | 74.3067 | 76.741 | 73.2046 | 81 | 84.2869 | 49.656 | 84.2869 | 73.1992 | 47.31% | 88.97
Oct | 236.452 | 263.3394 | 260.557 | 266.6179 | 284 | 282.0412 | 236.452 | 284 | 265.5012 | 17.91% | 281.91
Nov | 300.464 | 323.9542 | 301.917 | 328.2722 | 343 | 327.567 | 300.464 | 343 | 320.8624 | 13.26% | 324.29
Dec | 368.904 | 427.2521 | 383.54 | 427.8615 | 442 | 424.189 | 368.904 | 442 | 412.2911 | 17.73% | 417.43
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Month | [6 empty] | Min | Max | Mean | Mean** (%)
Jan | 402.0859 | 486.2194 | 384.437 | 468.5175 | 481 | 450.377 | 384.437 | 486.2194 | 445.4395 | 22.85% | 425.87
Feb | 325.1913 | 379.1855 | 310.691 | 375.159 | 387 | 358.1606 | 310.691 | 387 | 355.8979 | 21.44% | 347.46
Mar | 363.9118 | 405.8019 | 369.838 | 418.9749 | 433 | 406.8332 | 363.9118 | 433 | 399.7267 | 17.28% | 394.99
Apr | 189.356 | 207.8222 | 211.901 | 221.9916 | 241 | 219.3045 | 189.356 | 241 | 215.2292 | 23.99% | 218.78
May | 211.6059 | 203.3476 | 209.99 | 225.4265 | 239 | 226.7991 | 203.3476 | 239 | 219.3615 | 16.25% | 222.29
Jun | 130.8044 | 125.1506 | 117.966 | 138.2706 | 146 | 150.238 | 117.966 | 150.238 | 134.7383 | 23.95% | 137.79
Jul | 127.5038 | 125.4308 | 117.004 | 137.6771 | 146 | 148.876 | 117.004 | 148.876 | 133.7486 | 23.83% | 135.57
Aug | 125.5566 | 120.8271 | 110.949 | 138.1839 | 143 | 146.57 | 110.949 | 146.57 | 130.8478 | 27.22% | 128.66
Sep | 206.9339 | 221.1635 | 205.978 | 240.871 | 251 | 251.615 | 205.978 | 251.615 | 229.5936 | 19.88% | 227.77
Oct | 332.212 | 370.5637 | 341.56 | 382.6032 | 400 | 388.63 | 332.212 | 400 | 369.2615 | 18.36% | 361.45
Nov | 321.6299 | 374.2554 | 320.933 | 369.6986 | 381 | 358.3914 | 320.933 | 381 | 354.318 | 16.95% | 342.85
Dec | 371.2084 | 429.5306 | 348.155 | 420.9241 | 428 | 406.6018 | 348.155 | 429.5306 | 400.7366 | 20.31% | 385.77
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Month | [6 empty] | Min | Max | Mean | Mean** (%)
Jan | 0.778 | 0.94282 | 0.858 | 1.0748 | 1.03 | 0.98026 | 0.778 | 1.0748 | 0.94397 | 31.44% | 1.031
Feb | 0.49 | 0.45628 | 0.469 | 0.37915 | 0.51 | 0.4467 | 0.37915 | 0.51 | 0.45852 | 28.54% | 0.458
Mar | 0.501 | 0.42158 | 0.419 | 0.37021 | 0.47 | 0.42882 | 0.37021 | 0.501 | 0.4351 | 30.06% | 0.427
Apr | 0.449 | 0.43669 | 0.513 | 0.31865 | 0.45 | 0.42125 | 0.31865 | 0.513 | 0.43143 | 45.05% | 0.427
May | 0.35 | 0.44976 | 0.445 | 0.35588 | 0.52 | 0.45382 | 0.35 | 0.52 | 0.42908 | 39.62% | 0.431
Jun | 0.805 | 0.77848 | 0.748 | 0.73243 | 0.76 | 0.8526 | 0.73243 | 0.8526 | 0.77942 | 15.42% | 0.905
Jul | 0.599 | 0.53975 | 0.512 | 0.51445 | 0.57 | 0.61893 | 0.512 | 0.61893 | 0.55902 | 19.13% | 0.673
Aug | 0.572 | 0.55338 | 0.532 | 0.47852 | 0.56 | 0.59085 | 0.47852 | 0.59085 | 0.54779 | 20.5% | 0.624 | 0 | -0.40023 | -0.40371 | -0.38216 | 0.01327 | 0 | 0 | 6
Sep | 1.116 | 1.1204 | 1.114 | 1.0654 | 1.19 | 1.0172 | 1.0172 | 1.19 | 1.1038 | 15.66% | 1.08 | 7 | 0.63519 | 0.86207 | 0.75906 | 0.037066 | -5 | -17 | 7
Oct | 0.501 | 0.43546 | 0.461 | 0.35615 | 0.56 | 0.4821 | 0.35615 | 0.56 | 0.46595 | 43.75% | 0.46 | 7 | -1.2426 | -1.2329 | -1.1996 | 0.069211 | -5 | -17 | 8
Nov | 0.828 | 0.76387 | 0.73 | 0.78997 | 0.83 | 0.74371 | 0.73 | 0.83 | 0.78092 | 12.81% | 0.723 | 0 | 0.011624 | 0.015534 | -0.0003502 | 0.00124 | 0 | 0 | 9
Dec | 1.051 | 1.0145 | 0.991 | 1.0296 | 1.13 | 1.098 | 0.991 | 1.13 | 1.0523 | 13.21% | 1.062 | 7 | -1.2365 | -1.2364 | -1.1828 | 0.06368 | -5 | -17 | 1
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Month | [6 empty] | Min | Max | Mean | Mean** (%)
Jan | 3.668 | 4.2394 | 3.785 | 4.2737 | 4.38 | 4.1681 | 3.668 | 4.38 | 4.0857 | 17.43% | 3.591
Feb | 3.8251 | 4.3966 | 3.856 | 4.5578 | 4.57 | 4.326 | 3.8251 | 4.57 | 4.2553 | 17.51% | 3.768
Mar | 2.9499 | 3.7143 | 3.109 | 3.5155 | 3.77 | 3.3142 | 2.9499 | 3.77 | 3.3955 | 24.15% | 2.765
Apr | 2.3805 | 3.3839 | 2.568 | 2.9781 | 3.09 | 2.9655 | 2.3805 | 3.3839 | 2.8943 | 34.67% | 2.577
May | 1.2191 | 1.6524 | 1.448 | 1.5525 | 1.64 | 1.5759 | 1.2191 | 1.6524 | 1.5147 | 28.61% | 1.367
Jun | 1.1516 | 1.3521 | 1.194 | 1.4832 | 1.54 | 1.405 | 1.1516 | 1.54 | 1.3543 | 28.68% | 1.308
Jul | 1.1787 | 1.3473 | 1.325 | 1.5603 | 1.67 | 1.5217 | 1.1787 | 1.67 | 1.4338 | 34.26% | 1.387
Aug | 1.5602 | 1.6343 | 1.826 | 2.1462 | 2.19 | 2.1168 | 1.5602 | 2.19 | 1.9122 | 32.94% | 1.93
Sep | 2.125 | 2.3135 | 2.355 | 2.726 | 2.77 | 2.5488 | 2.125 | 2.77 | 2.473 | 26.08% | 2.362 | 0 | -2.079 | -2.548 | -2.4591 | -0.010291 | 0 | 0
Oct | 2.5377 | 2.8938 | 2.729 | 3.1817 | 3.17 | 2.9825 | 2.5377 | 3.1817 | 2.9158 | 22.09% | 2.824 | 0 | 0.417 | 0.44432 | 0.42125 | -0.0072513 | 0 | 0
Nov | 3.4939 | 3.9162 | 3.546 | 4.1922 | 4.09 | 3.8834 | 3.4939 | 4.1922 | 3.8536 | 18.12% | 3.429 | 0 | 0.339 | 0.57027 | 0.42213 | 0.024365 | 4 | 0
Dec | 3.468 | 4.3446 | 3.699 | 4.2828 | 4.45 | 4.2521 | 3.468 | 4.45 | 4.0828 | 24.05% | 3.669 | 0 | 0.649 | 0.67846 | 0.71889 | -0.014375 | 0 | 0
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## DATA for charts
Unformatted results for use in creating charts
Note: Enter tab name in row with purple background; data then flows here and elsewhere in this workbook as formulated.
| Tab Name==> | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | Trnsys | TestSpecAlt | K | K | K | K | K | K | K | K | K | YourData
| Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
Organization or Country:
| Label for Charts: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
| ANNUAL LOADS | [21 empty] | LOW MASS QUALIFICATION TESTS
| ANNUAL HEATING [MWH] | [21 empty] | ANNUAL HEATING [MWH]
0 | [17 empty] | 0 | MIN | MAX |  | CASES | [17 empty] | MIN | MAX
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE
105 | 395 Solid Conduction | 4.565 | 4.855 | 5.145 | 4.6412 | 4.8657 | 4.9081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.0113 | #N/A | #N/A | #N/A | 610-600 Low Mass, Heating S. Shade | 0.113 | 0.073669 | 0.097 | 0.050431 | 0.165 | 0.08851 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0942 | #N/A | #N/A
109 | 430 High-Cond. Wall Elements | 5.171 | 5.454 | 5.954 | 5.6201 | 5.5449 | 5.8505 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.9253 | #N/A | #N/A | #N/A | 620-600 Low Mass, Heating E&W Orientation | 0.32 | 0.10084 | 0.25 | 0.1607 | 0.1523 | 0.21543 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.248 | #N/A | #N/A
70 | 600 South Windows | 4.05 | 3.9928 | 4.047 | 4.3244 | 4.362 | 4.5036 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.4561 | #N/A | #N/A | #N/A | 630-620 Low Mass, Heating E&W Shade | 0.553 | 0.26235 | 0.38 | 0.29847 | 0.5363 | 0.4196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.4053 | #N/A | #N/A
71 | 610 S. Windows + Overhang | 4.163 | 4.0664 | 4.144 | 4.3748 | 4.527 | 4.5921 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.5503 | #N/A | #N/A | #N/A | 640-600 Low Mass, Heating Heating Setback | -1.368 | -1.5895 | -1.428 | -1.6625 | -1.7076 | -1.8508 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.017 | #N/A | #N/A
72 | 620 East & West Windows | 4.37 | 4.0936 | 4.297 | 4.4851 | 4.5143 | 4.719 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.7041 | #N/A | #N/A | #N/A
73 | 630 E&W Windows + Overhang & Fins | 4.923 | 4.3559 | 4.677 | 4.7835 | 5.0506 | 5.1386 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.1094 | #N/A | #N/A | #N/A | 660-600 Low-E Windows, Heating | -0.476 | -0.3908 | -0.226 | -0.61764 | -0.575 | -0.71389 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5082 | #N/A | #N/A
74 | 640 Case 600 with Htg. Temp. Setback | 2.682 | 2.4032 | 2.619 | 2.6618 | 2.6544 | 2.6528 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4391 | #N/A | #N/A | #N/A | 670-600 Single-Pane Windows, Heating | 1.434 | 1.3074 | 1.526 | 1.2918 | 1.613 | 1.6363 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4612 | #N/A | #N/A
75 | 650 Case 600 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 680-600 Case 600 with Greater Insulation | -1.831 | -2.2067 | -2.315 | -2.1447 | -2.2299 | -2.2173 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.2355 | #N/A | #N/A
| New Cases 660 to 695 and 980 to 995 | [20 empty] | 685-600 Case 600 with 20/20 Tstat | 0.482 | 0.58167 | 0.599 | 0.55275 | 0.5415 | 0.53862 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.5887 | #N/A | #N/A
0 | [18 empty] | MIN | MAX |  | 695-685 Case 685 with Greater Insulation | -1.823 | -2.1592 | -2.261 | -2.0752 | -2.1714 | -2.1504 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.1481 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 980-900 Case 900 with Greater Insulation | -1.006 | -1.1331 | -1.325 | -1.2527 | -1.2336 | -1.3636 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.3597 | #N/A | #N/A
70 | 600 South Windows | 4.05 | 3.9928 | 4.047 | 4.3244 | 4.362 | 4.5036 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.4561 | #N/A | #N/A | #N/A | 985-900 Case 900 with 20/20 Tstat | 1.075 | 0.74132 | 0.688 | 0.70563 | 0.6986 | 0.72238 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.778 | #N/A | #N/A
76 | 660 Low-E Windows | 3.574 | 3.602 | 3.821 | 3.7067 | 3.787 | 3.7897 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.9479 | #N/A | #N/A | #N/A | 995-985 Case 985 with Greater Insulation | -1.471 | -1.365 | -1.509 | -1.3628 | -1.3785 | -1.4594 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.5237 | #N/A | #N/A
77 | 670 Single-Pane Windows | 5.484 | 5.3002 | 5.573 | 5.6161 | 5.975 | 6.1399 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.9173 | #N/A | #N/A | #N/A
78 | 680 Case 600 with Greater Insulation | 2.219 | 1.7861 | 1.732 | 2.1797 | 2.1321 | 2.2863 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.2206 | #N/A | #N/A | #N/A
79 | 685 Case 600 with 20/20 Tstat | 4.532 | 4.5744 | 4.646 | 4.8771 | 4.9035 | 5.0422 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.0448 | #N/A | #N/A | #N/A
80 | 695 Case 685 with Greater Insulation | 2.709 | 2.4153 | 2.385 | 2.8019 | 2.7321 | 2.8917 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.8967 | #N/A | #N/A | #N/A
81 | 900 South Windows | 1.726 | 1.3789 | 1.591 | 1.6637 | 1.5847 | 1.814 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7651 | #N/A | #N/A | #N/A
88 | 980 Case 900 with Greater Insulation | 0.72 | 0.24577 | 0.266 | 0.41094 | 0.3511 | 0.45047 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.4054 | #N/A | #N/A | #N/A
89 | 985 Case 900 with 20/20 Tstat | 2.801 | 2.1202 | 2.279 | 2.3693 | 2.2833 | 2.5364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.5431 | #N/A | #N/A | #N/A
90 | 995 Case 985 with Greater Insulation | 1.33 | 0.75518 | 0.77 | 1.0065 | 0.9048 | 1.077 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0194 | #N/A | #N/A | #N/A
[22 empty] | ANNUAL COOLING [MWH] | [17 empty] | RANGE | RANGE
[19 empty] | MIN | MAX |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 610-600 Low Mass, Cooling S. Shade | -1.523 | -1.5313 | -1.259 | -1.6943 | -1.9293 | -1.6627 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4831 | #N/A | #N/A
114 | 800 High-Cond. Wall Elements | 5.141 | 4.9057 | 5.403 | 5.1156 | 4.9798 | 5.3695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.4287 | #N/A | #N/A | #N/A | 620-600 Low Mass, Cooling E&W Orientation | -1.418 | -1.8338 | -1.523 | -1.9675 | -1.9161 | -1.9389 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8457 | #N/A | #N/A
81 | 900 South Windows | 1.726 | 1.3789 | 1.591 | 1.6637 | 1.5847 | 1.814 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7651 | #N/A | #N/A | #N/A | 630-620 Low Mass, Cooling E&W Shade | -1.33 | -1.0589 | -1.122 | -1.2235 | -1.6504 | -1.2678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2328 | #N/A | #N/A
82 | 910 S. Windows + Overhang | 2.163 | 1.6477 | 1.86 | 1.9557 | 2.0672 | 2.1318 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.0799 | #N/A | #N/A | #N/A | 640-600 Low Mass, Cooling Heating Setback | -0.018 | -0.26921 | -0.195 | -0.26394 | -0.2692 | -0.3023 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3775 | #N/A | #N/A
83 | 920 East & West Windows | 3.5 | 2.9561 | 3.259 | 3.3365 | 3.2997 | 3.6067 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.5573 | #N/A | #N/A | #N/A | 650-600 Low Mass, Cooling Night Ventilation | -1.193 | -1.2592 | -1.246 | -1.2103 | -1.2167 | -1.1472 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1614 | #N/A | #N/A
84 | 930 E&W Windows + Overhang & Fins | 4.27 | 3.5236 | 3.933 | 3.9938 | 4.2776 | 4.3841 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.3184 | #N/A | #N/A | #N/A
85 | 940 Case 900 with Htg. Temp. Setback | 1.389 | 0.86324 | 1.149 | 1.0674 | 1.0147 | 1.1691 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0773 | #N/A | #N/A | #N/A | 660-600 Low-E Windows, Cooling | -2.808 | -2.5734 | -2.172 | -2.7955 | -2.9432 | -2.8133 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.6578 | #N/A | #N/A
86 | 950 Case 900 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 670-600 Single-Pane Windows, Cooling | 0.717 | 0.66462 | 0.522 | 0.59566 | 0.3585 | 0.41828 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.217 | #N/A | #N/A
87 | 960 Sunspace | #N/A | 2.5221 | 2.771 | 2.689 | 2.6239 | 2.8595 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.0413 | #N/A | #N/A | #N/A | 680-600 Case 600 with Greater Insulation | 0.116 | 0.51669 | 0.5 | 0.41686 | 0.3676 | 0.53023 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.6054 | #N/A | #N/A
[22 empty] | 685-600 Case 600 with 20/20 Tstat | 3.308 | 2.9461 | 2.806 | 3.0918 | 2.9596 | 3.0718 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.0107 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 695-685 Case 685 with Greater Insulation | -0.375 | 0.1149 | 0.148 | 0.052759 | 0.0276 | 0.18778 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.301 | #N/A | #N/A
91 | 195 Solid Conduction | 4.217 | 3.9901 | 4.157 | 4.0696 | 3.9509 | 4.0939 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.1143 | #N/A | #N/A | #N/A | 980-900 Case 900 with Greater Insulation | 0.787 | 1.5314 | 1.375 | 1.2231 | 1.2868 | 1.2514 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.3242 | #N/A | #N/A
92 | 200 Surface Convection Int IR="off" Ext IR="off" | 5.041 | 4.8135 | 5.226 | 5.1054 | 4.9204 | 5.1429 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.1278 | #N/A | #N/A | #N/A | 985-900 Case 900 with 20/20 Tstat | 4.559 | 3.7698 | 3.497 | 3.8704 | 3.7616 | 3.8463 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.8589 | #N/A | #N/A
93 | 210 Infrared Radiation Int IR="off" Ext IR="on" | 5.627 | 5.9663 | 6.531 | 6.0466 | 6.3171 | 6.4295 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.3295 | #N/A | #N/A | #N/A | 995-985 Case 985 with Greater Insulation | 0.209 | 0.9685 | 0.891 | 0.84367 | 0.8995 | 0.95032 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9106 | #N/A | #N/A
94 | 215 Infrared Radiation Int IR="on" Ext IR="off" | 5.652 | 5.3066 | 5.697 | 5.4054 | 5.1811 | 5.4434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.5973 | #N/A | #N/A | #N/A
95 | 220 In-Depth Base Case | 6.377 | 6.6663 | 7.178 | 6.4551 | 6.7257 | 6.8678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.9918 | #N/A | #N/A | #N/A
96 | 230 Infiltration | 9.851 | 9.8124 | 10.417 | 9.9299 | 9.9385 | 10.2343 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10.3855 | #N/A | #N/A | #N/A
97 | 240 Internal Gains | 5.116 | 5.4426 | 5.944 | 5.2794 | 5.5393 | 5.6572 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.7694 | #N/A | #N/A | #N/A
98 | 250 Exterior Solar Absorptance | 4.733 | 5.0438 | 5.373 | 4.8991 | 4.935 | 5.1047 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.2644 | #N/A | #N/A | #N/A | [18 empty] | RANGE | RANGE
PEAK HEATING [KW]
[22 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
[22 empty] | 610-600 Low Mass, Heating S. Shade | -0.089 | 0.000526 | 0.004 | -0.012584 | 0.005 | 0.00060921 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.004 | #N/A | #N/A
[22 empty] | 620-600 Low Mass, Heating E&W Orientation | -0.11 | 0.017627 | 0.033 | 0.024696 | 0.025 | 0.025699 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.05 | #N/A | #N/A
[22 empty] | 630-620 Low Mass, Heating E&W Shade | 0.107 | 0.001512 | 0.004 | -0.022564 | 0.006 | 0.0029619 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.006 | #N/A | #N/A
[22 empty] | 640-600 Low Mass, Heating Heating Setback | 1.378 | 1.2022 | 1.623 | 1.3541 | 0.873 | 0.67965 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.102 | #N/A | #N/A
[22 empty] | 660-600 Low-E Windows, Cooling | -0.635 | -0.26192 | -0.237 | -0.3733 | -0.382 | -0.40371 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.335 | #N/A | #N/A
[22 empty] | 670-600 Single-Pane Windows, Cooling | 0.867 | 0.63519 | 0.777 | 0.6491 | 0.764 | 0.86207 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.68 | #N/A | #N/A
[22 empty] | 680-600 Case 600 with Greater Insulation | -1.129 | -1.2426 | -1.224 | -1.152 | -1.206 | -1.2442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.111 | #N/A | #N/A
[22 empty] | 685-600 Case 600 with 20/20 Tstat | -0.086 | 0.011624 | 0.019 | 0.018741 | 0.019 | 0.015534 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.028 | #N/A | #N/A
[22 empty] | 695-685 Case 685 with Greater Insulation | -1.031 | -1.2365 | -1.199 | -1.1514 | -1.222 | -1.2567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.133 | #N/A | #N/A
[22 empty] | 980-900 Case 900 with Greater Insulation | -0.858 | -1.1896 | -1.071 | -1.1497 | -1.16 | -1.1863 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.026 | #N/A | #N/A
[22 empty] | 985-900 Case 900 with 20/20 Tstat | 0.203 | 0.008773 | 0.005 | 0.0079536 | 0.009 | 0.0069624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.006 | #N/A | #N/A
[22 empty] | 995-985 Case 985 with Greater Insulation | -1.043 | -1.0826 | -0.996 | -1.0733 | -1.082 | -1.1235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.981 | #N/A | #N/A
[22 empty] | PEAK COOLING [KW] | [17 empty] | RANGE | RANGE
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
99 | 270 South Windows | #N/A | 4.3465 | 4.273 | 4.3854 | 4.5764 | 4.6312 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.6181 | #N/A | #N/A | #N/A | [18 empty] | RANGE | RANGE
100 | 280 Cavity Albedo | #N/A | 4.5249 | 4.619 | 4.5701 | 4.7381 | 4.8699 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.9163 | #N/A | #N/A | #N/A | 610-600 Low Mass, Cooling S. Shade | -0.184 | -0.048825 | -0.091 | -0.21703 | -0.259 | -0.17795 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.265 | #N/A | #N/A
101 | 290 South Shading | #N/A | 4.4242 | 4.381 | 4.4244 | 4.7447 | 4.7248 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.7191 | #N/A | #N/A | #N/A | 620-600 Low Mass, Cooling E&W Orientation | -0.946 | -1.9882 | -1.467 | -1.5541 | -1.571 | -1.4575 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.373 | #N/A | #N/A
102 | 300 East/West Windows | #N/A | 4.3184 | 4.46 | 4.4245 | 4.6679 | 4.7256 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.7466 | #N/A | #N/A | #N/A | 630-620 Low Mass, Cooling E&W Shade | -0.583 | -0.49451 | -0.429 | -0.58526 | -0.651 | -0.63889 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.605 | #N/A | #N/A
103 | 310 East/West Shading | #N/A | 4.5803 | 4.846 | 4.6912 | 5.2396 | 5.1626 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.1592 | #N/A | #N/A | #N/A | 640-600 Low Mass, Cooling Heating Setback | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
104 | 320 Thermostat | #N/A | 3.6775 | 3.599 | 3.7712 | 3.9699 | 4.0311 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.9635 | #N/A | #N/A | #N/A | 650-600 Low Mass, Cooling Night Ventilation | -0.002 | -0.19129 | -0.377 | -0.21342 | -0.232 | -0.24825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.168 | #N/A | #N/A
[22 empty] | 660-600 Low-E Windows, Cooling | -2.307 | -2.548 | -2.067 | -2.5812 | -2.663 | -2.5883 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.174 | #N/A | #N/A
[22 empty] | 670-600 Single-Pane Windows, Cooling | 0.567 | 0.44432 | 0.417 | 0.45463 | 0.289 | 0.35556 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.332 | #N/A | #N/A
[22 empty] | 680-600 Case 600 with Greater Insulation | 0.111 | 0.57027 | 0.439 | 0.41866 | 0.483 | 0.51086 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.419 | #N/A | #N/A
[22 empty] | 685-600 Case 600 with 20/20 Tstat | 0.668 | 0.67846 | 0.649 | 0.7552 | 0.741 | 0.82169 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.679 | #N/A | #N/A
[22 empty] | 695-685 Case 685 with Greater Insulation | -0.086 | 0.38129 | 0.284 | 0.22753 | 0.305 | 0.30772 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.33 | #N/A | #N/A
[22 empty] | 980-900 Case 900 with Greater Insulation | 0.345 | 0.29156 | 0.374 | 0.40968 | 0.445 | 0.37249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.339 | #N/A | #N/A
[22 empty] | 985-900 Case 900 with 20/20 Tstat | 0.938 | 0.84883 | 0.652 | 0.87434 | 0.84 | 0.94464 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.698 | #N/A | #N/A
[22 empty] | 995-985 Case 985 with Greater Insulation | 0.152 | -0.001482 | 0.107 | 0.26266 | 0.218 | 0.2302 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.127 | #N/A | #N/A
High Mass QUALIFICATION TESTS
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | ANNUAL HEATING [MWH] | [17 empty] | RANGE | RANGE
105 | 395 Low Mass Solid Conduction | 4.565 | 4.855 | 5.145 | 4.6412 | 4.8657 | 4.9081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.0113 | #N/A | #N/A | #N/A | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
106 | 400 Low Mass High-Cond. Wall Elements | 5.906 | 6.5358 | 7.047 | 6.3478 | 6.61 | 6.7692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.8634 | #N/A | #N/A | #N/A | 900-600 Mass, Heating | -2.324 | -2.6139 | -2.456 | -2.6607 | -2.7773 | -2.6895 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.691 | #N/A | #N/A
107 | 410 Low Mass Infiltration | 7.63 | 8.0451 | 8.661 | 8.0803 | 8.2122 | 8.4449 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 8.5515 | #N/A | #N/A | #N/A | 920-900 High Mass, Heating E&W Orientation | 1.774 | 1.5772 | 1.668 | 1.6728 | 1.715 | 1.7927 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7922 | #N/A | #N/A
108 | 420 Low Mass Internal Gains | 6.399 | 6.8345 | 7.433 | 6.9058 | 7.027 | 7.2364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.3346 | #N/A | #N/A | #N/A | 910-900 High Mass, Heating S. Shade | 0.437 | 0.26879 | 0.269 | 0.29205 | 0.4825 | 0.31776 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.3148 | #N/A | #N/A
109 | 430 Low Mass Ext. Shortwave Absorptance | 5.171 | 5.454 | 5.954 | 5.6201 | 5.5449 | 5.8505 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.9253 | #N/A | #N/A | #N/A | 930-920 High Mass, Heating E&W Shade | 0.77 | 0.56758 | 0.674 | 0.6573 | 0.9779 | 0.7774 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.7611 | #N/A | #N/A
110 | 440 Low Mass Cavity Albedo | #N/A | 4.1559 | 4.33 | 4.5001 | 4.5039 | 4.7207 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.7094 | #N/A | #N/A | #N/A | 940-900 High Mass, Heating Heating Setback | -0.337 | -0.51566 | -0.442 | -0.5963 | -0.57 | -0.6449 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6878 | #N/A | #N/A
111 | 450 Const. Int.&Ext. Surf. Coefs., Heating | 3.743 | 3.9904 | 3.375 | 3.9625 | 3.8503 | 3.8709 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.8052 | #N/A | #N/A | #N/A
112 | 460 Const. Interior Surf. Coefs., Heating | 3.828 | 4.0555 | 3.873 | 4.1938 | 4.2625 | 4.2898 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.2031 | #N/A | #N/A | #N/A | 960-900 High Mass, Heating Sunspace | #N/A | 1.1432 | 1.18 | 1.0254 | 1.0392 | 1.0455 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2762 | 0.775 | 1.718
113 | 470 Const. Exterior Surf. Coefs., Heating | 4.042 | 3.8995 | 3.54 | 4.0939 | 3.9597 | 4.0746 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.0547 | #N/A | #N/A | #N/A
114 | 800 High Mass High-Cond. Wall Elements | 5.141 | 4.9057 | 5.403 | 5.1156 | 4.9798 | 5.3695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.4287 | #N/A | #N/A | #N/A
115 | 810 High Mass Cavity Albedo | #N/A | 2.0375 | 2.454 | 2.3418 | 2.185 | 2.6098 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.5434 | #N/A | #N/A | #N/A
ANNUAL COOLING [MWH]
0 | CASE# | [17 empty] | MIN | MAX |  | ANNUAL COOLING [MWH] | [17 empty] | RANGE | RANGE
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
105 | 395 Solid Conduction | 0.021 | 0.007762 | 0.006 | 0.01038 | 0.0055 | 0.0035162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0048 | #N/A | #N/A | #N/A | 900-600 Mass, Cooling | -3.108 | -3.4493 | -3.049 | -3.5383 | -3.6741 | -3.5124 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.3292 | #N/A | #N/A
109 | 430 High-Cond. Wall Elements | 1.084 | 0.90616 | 0.944 | 0.85562 | 0.9527 | 0.73902 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.7501 | #N/A | #N/A | #N/A | 910-900 High Mass, Cooling S. Shade | -1.23 | -1.049 | -0.893 | -1.1053 | -1.2048 | -1.0763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0162 | #N/A | #N/A
70 | 600 South Windows | 5.822 | 5.9131 | 5.432 | 6.027 | 6.1618 | 5.7795 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.7898 | #N/A | #N/A | #N/A | 920-900 High Mass, Cooling E&W Orientation | 0.414 | 0.32538 | 0.323 | 0.2421 | 0.3267 | 0.28174 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2095 | #N/A | #N/A
71 | 610 S. Windows + Overhang | 4.299 | 4.3818 | 4.173 | 4.3328 | 4.2325 | 4.1168 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.3067 | #N/A | #N/A | #N/A | [18 empty] | 0 | 0
72 | 620 East & West Windows | 4.404 | 4.0793 | 3.909 | 4.0595 | 4.2457 | 3.8407 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.9441 | #N/A | #N/A | #N/A | 960-900 High Mass, Cooling Sunspace | #N/A | -1.538 | -1.474 | -1.5816 | -1.5381 | -1.4782 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.6476 | #N/A | #N/A
73 | 630 E&W Windows + Overhang & Fins | 3.074 | 3.0204 | 2.787 | 2.836 | 2.5953 | 2.5729 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.7113 | #N/A | #N/A | #N/A | 930-920 High Mass, Cooling E&W Shade | -0.967 | -0.71422 | -0.798 | -0.81173 | -1.1606 | -0.87711 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.8688 | #N/A | #N/A
74 | 640 Case 600 with Htg. Temp. Setback | 5.804 | 5.6439 | 5.237 | 5.7631 | 5.8926 | 5.4772 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.4123 | #N/A | #N/A | #N/A | 940-900 High Mass, Cooling Heating Setback | -0.101 | -0.06725 | -0.04 | -0.06439 | -0.0601 | -0.06367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0823 | #N/A | #N/A
75 | 650 Case 600 with Night Ventilation | 4.629 | 4.6539 | 4.186 | 4.8168 | 4.9451 | 4.6323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.6284 | #N/A | #N/A | #N/A | 950-900 High Mass, Cooling Night Ventilation | -2.128 | -1.8658 | -1.765 | -1.7818 | -1.8317 | -1.6255 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.7097 | #N/A | #N/A
[22 empty] | 960-900 High Mass, Cooling Sunspace | #N/A | -1.538 | -1.474 | -1.5816 | -1.5381 | -1.4782 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.6476 | #N/A | #N/A
New Cases 660 to 695 and 980 to 995
[19 empty] | MIN | MAX
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE
70 | 600 South Windows | 5.822 | 5.9131 | 5.432 | 6.027 | 6.1618 | 5.7795 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.7898 | #N/A | #N/A | #N/A
76 | 660 Low-E Windows | 3.014 | 3.3397 | 3.26 | 3.2315 | 3.2186 | 2.9663 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.132 | #N/A | #N/A | #N/A
77 | 670 Single-Pane Windows | 6.539 | 6.5777 | 5.954 | 6.6227 | 6.5203 | 6.1978 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.0068 | #N/A | #N/A | #N/A
78 | 680 Case 600 with Greater Insulation | 5.938 | 6.4298 | 5.932 | 6.4439 | 6.5294 | 6.3098 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.3952 | #N/A | #N/A | #N/A
79 | 685 Case 600 with 20/20 Tstat | 9.13 | 8.8592 | 8.238 | 9.1188 | 9.1214 | 8.8513 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 8.8005 | #N/A | #N/A | #N/A
80 | 695 Case 685 with Greater Insulation | 8.755 | 8.9741 | 8.386 | 9.1716 | 9.149 | 9.0391 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.1015 | #N/A | #N/A | #N/A
81 | 900 South Windows | 2.714 | 2.4638 | 2.383 | 2.4887 | 2.4877 | 2.2671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4606 | #N/A | #N/A | #N/A
88 | 980 Case 900 with Greater Insulation | 3.501 | 3.9953 | 3.758 | 3.7118 | 3.7745 | 3.5185 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.7848 | #N/A | #N/A | #N/A
89 | 985 Case 900 with 20/20 Tstat | 7.273 | 6.2336 | 5.88 | 6.3592 | 6.2493 | 6.1135 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.3195 | #N/A | #N/A | #N/A
90 | 995 Case 985 with Greater Insulation | 7.482 | 7.2022 | 6.771 | 7.2029 | 7.1488 | 7.0638 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.2301 | #N/A | #N/A | #N/A
[19 empty] | MIN | MAX
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE
114 | 800 High-Cond. Wall Elements | 0.473 | 0.37983 | 0.362 | 0.37353 | 0.3914 | 0.28208 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2682 | #N/A | #N/A | #N/A
81 | 900 South Windows | 2.714 | 2.4638 | 2.383 | 2.4887 | 2.4877 | 2.2671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4606 | #N/A | #N/A | #N/A | PEAK HEATING [KW] | [17 empty] | RANGE | RANGE
82 | 910 S. Windows + Overhang | 1.484 | 1.4149 | 1.49 | 1.3835 | 1.2829 | 1.1909 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4444 | #N/A | #N/A | #N/A | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
83 | 920 East & West Windows | 3.128 | 2.7892 | 2.706 | 2.7308 | 2.8144 | 2.5489 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.6701 | #N/A | #N/A | #N/A | [18 empty] | RANGE | RANGE
84 | 930 E&W Windows + Overhang & Fins | 2.161 | 2.075 | 1.908 | 1.9191 | 1.6538 | 1.6718 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.8013 | #N/A | #N/A | #N/A | 900-600 Mass, Heating | -0.704 | -0.57684 | -0.582 | -0.51694 | -0.595 | -0.58042 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.526 | #N/A | #N/A
85 | 940 Case 900 with Htg. Temp. Setback | 2.613 | 2.3966 | 2.343 | 2.4244 | 2.4276 | 2.2035 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.3783 | #N/A | #N/A | #N/A | 910-900 High Mass, Heating S. Shade | 0.21 | 0.025635 | 0.021 | 0.011437 | 0.051 | 0.020717 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.02 | #N/A | #N/A
86 | 950 Case 900 with Night Ventilation | 0.586 | 0.59803 | 0.618 | 0.70692 | 0.656 | 0.64162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.7509 | #N/A | #N/A | #N/A | 920-900 High Mass, Heating E&W Orientation | 0.344 | 0.069036 | 0.06 | 0.08269 | 0.073 | 0.085796 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.076 | #N/A | #N/A
87 | 960 Sunspace | #N/A | 0.92578 | 0.909 | 0.90712 | 0.9496 | 0.78896 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.813 | #N/A | #N/A | #N/A | 930-920 High Mass, Heating E&W Shade | 0.073 | 0.024542 | 0.036 | 0.014719 | 0.059 | 0.03614 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.033 | #N/A | #N/A
[22 empty] | 940-900 High Mass, Heating Heating Setback | 1.331 | 0.60852 | 1.206 | 0.45528 | 0.489 | 0.62635 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.807 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 960-900 High Mass, Heating Sunspace | #N/A | -0.31135 | -0.368 | -0.42812 | -0.432 | -0.47808 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.374 | #N/A | #N/A
91 | 195 Solid Conduction | 0.712 | 0.60552 | 0.628 | 0.61152 | 0.611 | 0.59153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.6299 | #N/A | #N/A | #N/A
92 | 200 Surface Convection Int IR="off" Ext IR="off" | 0.839 | 0.80024 | 0.835 | 0.81408 | 0.8004 | 0.78844 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8345 | #N/A | #N/A | #N/A
93 | 210 Infrared Radiation Int IR="off" Ext IR="on" | 0.688 | 0.50307 | 0.496 | 0.5599 | 0.5185 | 0.45918 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.5009 | #N/A | #N/A | #N/A | [18 empty] | RANGE | RANGE
94 | 215 Infrared Radiation Int IR="on" Ext IR="off" | 0.952 | 0.94579 | 0.922 | 0.87747 | 0.8948 | 0.85047 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9223 | #N/A | #N/A | #N/A | PEAK COOLING [KW] | [17 empty] | RANGE | RANGE
95 | 220 In-Depth Base Case | 0.803 | 0.6106 | 0.55 | 0.6099 | 0.5762 | 0.49766 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.5591 | #N/A | #N/A | #N/A | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
96 | 230 Infiltration | 1.184 | 0.99134 | 0.929 | 0.99121 | 0.955 | 0.89664 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9645 | #N/A | #N/A | #N/A | 900-600 Mass, Cooling | -2.611 | -3.1046 | -2.866 | -3.3111 | -3.297 | -3.1057 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.791 | #N/A | #N/A
97 | 240 Internal Gains | 1.287 | 0.98237 | 0.876 | 0.97875 | 0.9218 | 0.83378 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8915 | #N/A | #N/A | #N/A | 910-900 High Mass, Cooling S. Shade | -0.546 | -0.65436 | -0.453 | -0.81835 | -0.684 | -0.85903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.682 | #N/A | #N/A
98 | 250 Exterior Solar Absorptance | 3.612 | 3.429 | 3.471 | 3.1816 | 3.4668 | 2.9038 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.038 | #N/A | #N/A | #N/A | 920-900 High Mass, Cooling E&W Orientation | 0.442 | -0.31975 | 0.154 | 0.21988 | 0.203 | 0.21408 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.091 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 930-920 High Mass, Cooling E&W Shade | -0.429 | -0.39486 | -0.375 | -0.47881 | -0.605 | -0.54103 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.473 | #N/A | #N/A
99 | 270 South Windows | #N/A | 7.2708 | 6.698 | 7.5215 | 7.3086 | 7.2885 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.3166 | #N/A | #N/A | #N/A
100 | 280 Cavity Albedo | #N/A | 4.9963 | 4.215 | 5.1829 | 5.2058 | 4.8081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.0469 | #N/A | #N/A | #N/A | 940-900 High Mass, Cooling Heating Setback | 0.119 | 0 | 0 | -0.00048524 | -0.005 | -0.0024478 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
101 | 290 South Shading | #N/A | 5.6097 | 5.31 | 5.7425 | 5.3206 | 5.4612 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.705 | #N/A | #N/A | #N/A | 950-900 High Mass, Cooling Night Ventilation | -0.673 | -1.0129 | -0.502 | -0.65292 | -0.694 | -0.70368 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.481 | #N/A | #N/A
102 | 300 East/West Windows | #N/A | 5.0551 | 4.805 | 5.152 | 5.0381 | 4.913 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.0862 | #N/A | #N/A | #N/A | 960-900 High Mass, Cooling Sunspace | #N/A | -1.9993 | -1.189 | -1.5605 | -1.493 | -1.6016 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.46 | #N/A | #N/A
103 | 310 East/West Shading | #N/A | 3.7519 | 3.402 | 3.6695 | 3.1279 | 3.3242 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.5425 | #N/A | #N/A | #N/A
104 | 320 Thermostat | #N/A | 4.8585 | 4.42 | 4.986 | 4.9131 | 4.7877 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.8589 | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
105 | 395 Low Mass Solid Conduction | 0.021 | 0.007762 | 0.006 | 0.01038 | 0.0055 | 0.0035162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0048 | #N/A | #N/A | #N/A
106 | 400 Low Mass High-Cond. Wall Elements | 0.063 | 0.023304 | 0.017 | 0.030566 | 0.0244 | 0.012683 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0152 | #N/A | #N/A | #N/A
107 | 410 Low Mass Infiltration | 0.096 | 0.048491 | 0.041 | 0.057269 | 0.0523 | 0.03512 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0396 | #N/A | #N/A | #N/A
108 | 420 Low Mass Internal Gains | 0.228 | 0.14062 | 0.119 | 0.15257 | 0.1419 | 0.10944 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.117 | #N/A | #N/A | #N/A
109 | 430 Low Mass Ext. Shortwave Absorptance | 1.084 | 0.90616 | 0.944 | 0.85562 | 0.9527 | 0.73902 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.7501 | #N/A | #N/A | #N/A
110 | 440 Low Mass Cavity Albedo | #N/A | 3.9853 | 3.458 | 4.085 | 4.4141 | 3.7412 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.9235 | #N/A | #N/A | #N/A
111 | 450 Const. Int.&Ext. Surf. Coefs., Cooling | 6.172 | 5.689 | 6.161 | 6.5073 | 6.6132 | 6.5307 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.6733 | #N/A | #N/A | #N/A
112 | 460 Const. Interior Surf. Coefs., Cooling | 6.26 | 5.9398 | 5.929 | 6.4746 | 6.7291 | 6.2434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.358 | #N/A | #N/A | #N/A | Low Mass PRIMITIVE DIAGNOSTIC TESTS
113 | 470 Const. Exterior Surf. Coefs., Cooling | 5.987 | 5.6439 | 5.649 | 6.0294 | 6.0054 | 6.0559 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.0887 | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
114 | 800 High Mass High-Cond. Wall Elements | 0.473 | 0.37983 | 0.362 | 0.37353 | 0.3914 | 0.28208 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2682 | #N/A | #N/A | #N/A | CASES
115 | 810 High Mass Cavity Albedo | #N/A | 1.4807 | 1.357 | 1.5078 | 1.6056 | 1.2945 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4654 | #N/A | #N/A | #N/A | ANNUAL HEATING [MWH]
[22 empty] | 200-195 Heating Surface Convection | 0.824 | 0.82337 | 1.069 | 1.0358 | 0.9695 | 1.0489 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0135 | #N/A | #N/A
| ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS | [20 empty] | 210-200 Heating Ext IR (Int IR "off") | 0.586 | 1.1529 | 1.305 | 0.94118 | 1.3967 | 1.2866 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2017 | #N/A | #N/A
[22 empty] | 220-215 Heating Ext IR (Int IR "on") | 0.725 | 1.3597 | 1.481 | 1.0497 | 1.5446 | 1.4244 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.3945 | #N/A | #N/A
0 | COUNTRY: | [17 empty] | RANGE | RANGE |  | 215-200 Heating Int IR (Ext IR "off") | 0.611 | 0.49316 | 0.471 | 0.30004 | 0.2607 | 0.30051 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.4695 | #N/A | #N/A
KW | CASE# | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | MIN | MAX | AVERAGE | 220-210 Heating Int IR (Ext IR "on") | 0.75 | 0.70003 | 0.647 | 0.40857 | 0.4086 | 0.43834 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.6623 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
105 | 395 Solid Conduction | 1.948 | 2.1574 | 2.085 | 1.9517 | 2.09 | 2.1613 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.04 | #N/A | #N/A | #N/A
109 | 430 High-Cond. Wall Elements | 3.3 | 3.2539 | 3.36 | 3.3163 | 3.285 | 3.4088 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.283 | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
70 | 600 South Windows | 3.255 | 3.0202 | 3.035 | 3.2044 | 3.228 | 3.3589 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.198 | #N/A | #N/A | #N/A | 230-220 Heating Infiltration | 3.474 | 3.146 | 3.239 | 3.4747 | 3.2128 | 3.3665 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.3937 | #N/A | #N/A
71 | 610 S. Windows + Overhang | 3.166 | 3.0208 | 3.039 | 3.1918 | 3.233 | 3.3595 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.202 | #N/A | #N/A | #N/A | 240-220 Heating Internal Gains | -1.261 | -1.2237 | -1.234 | -1.1758 | -1.1864 | -1.2106 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2224 | #N/A | #N/A
72 | 620 East & West Windows | 3.145 | 3.0379 | 3.068 | 3.2291 | 3.253 | 3.3846 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.248 | #N/A | #N/A | #N/A | 250-220 Heating Ext Solar Absorptance | -1.644 | -1.6225 | -1.805 | -1.556 | -1.7907 | -1.7631 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.7274 | #N/A | #N/A
73 | 630 E&W Windows + Overhang & Fins | 3.252 | 3.0394 | 3.072 | 3.2066 | 3.259 | 3.3876 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.254 | #N/A | #N/A | #N/A | 270-220 Heating South Windows | #N/A | -2.3199 | -2.905 | -2.0698 | -2.1493 | -2.2367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.3737 | #N/A | #N/A
74 | 640 Case 600 with Htg. Temp. Setback | 4.633 | 4.2225 | 4.658 | 4.5585 | 4.101 | 4.0385 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.3 | #N/A | #N/A | #N/A | 280-270 Heating Cavity Albedo | #N/A | 0.17846 | 0.346 | 0.18472 | 0.1617 | 0.23873 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2982 | #N/A | #N/A
75 | 650 Case 600 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 290-270 Heating South Shading | #N/A | 0.077715 | 0.108 | 0.039046 | 0.1683 | 0.09362 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.101 | #N/A | #N/A
[22 empty] | 300-270 Heating E&W Windows | #N/A | -0.028118 | 0.187 | 0.039197 | 0.0915 | 0.09447 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1285 | #N/A | #N/A
| New Cases 660 to 695 and 980 to 995 | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
[19 empty] | MIN | MAX |  | 320-270 Heating Thermostat | #N/A | -0.66901 | -0.674 | -0.61416 | -0.6065 | -0.60003 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6546 | #N/A | #N/A
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 310-300 Heating E&W Shading | #N/A | 0.26199 | 0.386 | 0.26662 | 0.5717 | 0.43695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.4126 | #N/A | #N/A
70 | 600 South Windows | 3.255 | 3.0202 | 3.035 | 3.2044 | 3.228 | 3.3589 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.198 | #N/A | #N/A | #N/A
76 | 660 Low-E Windows | 2.62 | 2.7583 | 2.798 | 2.8311 | 2.846 | 2.9552 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.863 | #N/A | #N/A | #N/A
77 | 670 Single-Pane Windows | 4.122 | 3.6554 | 3.812 | 3.8535 | 3.992 | 4.221 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.878 | #N/A | #N/A | #N/A
78 | 680 Case 600 with Greater Insulation | 2.126 | 1.7776 | 1.811 | 2.0524 | 2.022 | 2.1147 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.087 | #N/A | #N/A | #N/A
79 | 685 Case 600 with 20/20 Tstat | 3.169 | 3.0319 | 3.054 | 3.2232 | 3.247 | 3.3744 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.226 | #N/A | #N/A | #N/A
80 | 695 Case 685 with Greater Insulation | 2.138 | 1.7953 | 1.855 | 2.0718 | 2.025 | 2.1177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.093 | #N/A | #N/A | #N/A
81 | 900 South Windows | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.633 | 2.7785 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.672 | #N/A | #N/A | #N/A
88 | 980 Case 900 with Greater Insulation | 1.693 | 1.2538 | 1.382 | 1.5378 | 1.473 | 1.5921 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.646 | #N/A | #N/A | #N/A
89 | 985 Case 900 with 20/20 Tstat | 2.754 | 2.4522 | 2.458 | 2.6954 | 2.642 | 2.7854 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.678 | #N/A | #N/A | #N/A
90 | 995 Case 985 with Greater Insulation | 1.711 | 1.3696 | 1.462 | 1.6221 | 1.56 | 1.662 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.697 | #N/A | #N/A | #N/A
[19 empty] | RANGE | RANGE
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX | AVERAGE
114 | 800 High-Cond. Wall Elements | 2.957 | 2.7776 | 2.864 | 2.9237 | 2.84 | 2.9669 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.846 | #N/A | #N/A | #N/A
81 | 900 South Windows | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.633 | 2.7785 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.672 | #N/A | #N/A | #N/A
82 | 910 S. Windows + Overhang | 2.761 | 2.469 | 2.474 | 2.6989 | 2.684 | 2.7992 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.692 | #N/A | #N/A | #N/A
83 | 920 East & West Windows | 2.895 | 2.5124 | 2.513 | 2.7702 | 2.706 | 2.8643 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.748 | #N/A | #N/A | #N/A | ANNUAL COOLING [MWH]
84 | 930 E&W Windows + Overhang & Fins | 2.968 | 2.537 | 2.549 | 2.7849 | 2.765 | 2.9004 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.781 | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
85 | 940 Case 900 with Htg. Temp. Setback | 3.882 | 3.0519 | 3.659 | 3.1428 | 3.122 | 3.4048 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.479 | #N/A | #N/A | #N/A | CASES | [17 empty] | MIN | MAX
86 | 950 Case 900 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 200-195 Cooling Surface Convection | 0.127 | 0.19471 | 0.207 | 0.20256 | 0.1894 | 0.19691 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2046 | #N/A | #N/A
87 | 960 Sunspace | #N/A | 2.132 | 2.085 | 2.2594 | 2.201 | 2.3004 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.298 | #N/A | #N/A | #N/A | 210-200 Cooling Ext IR (Int IR "off") | -0.151 | -0.29717 | -0.339 | -0.25418 | -0.2819 | -0.32926 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3336 | #N/A | #N/A
[22 empty] | 220-215 Cooling Ext IR (Int IR "on") | -0.149 | -0.33519 | -0.372 | -0.26756 | -0.3186 | -0.35281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3632 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 215-200 Cooling Int IR (Ext IR "off") | 0.113 | 0.14556 | 0.087 | 0.063388 | 0.0944 | 0.062024 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0878 | #N/A | #N/A
91 | 195 Solid Conduction | 1.802 | 1.7907 | 1.799 | 1.7944 | 1.802 | 1.7959 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.733 | #N/A | #N/A | #N/A |  | 0.115 | 0.10753 | 0.054 | 0.050007 | 0.0577 | 0.038475 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0582 | #N/A | #N/A
92 | 200 Surface Convection Int IR="off" Ext IR="off" | 2.272 | 2.226 | 2.308 | 2.3413 | 2.275 | 2.3527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.185 | #N/A | #N/A | #N/A
93 | 210 Infrared Radiation Int IR="off" Ext IR="on" | 2.374 | 2.629 | 2.605 | 2.5646 | 2.671 | 2.7498 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.504 | #N/A | #N/A | #N/A | 230-220 Cooling Infiltration | 0.381 | 0.38074 | 0.379 | 0.38131 | 0.3788 | 0.39898 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.4054 | #N/A | #N/A
94 | 215 Infrared Radiation Int IR="on" Ext IR="off" | 2.521 | 2.42 | 2.52 | 2.4778 | 2.39 | 2.4894 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.407 | #N/A | #N/A | #N/A | 240-220 Cooling Internal Gains | 0.484 | 0.37177 | 0.326 | 0.36884 | 0.3456 | 0.33612 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.3324 | #N/A | #N/A
95 | 220 In-Depth Base Case | 2.631 | 2.8394 | 2.863 | 2.692 | 2.788 | 2.8786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.734 | #N/A | #N/A | #N/A | 250-220 Cooling Ext Solar Abs. | 2.809 | 2.8184 | 2.921 | 2.5717 | 2.8906 | 2.4062 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4789 | #N/A | #N/A
96 | 230 Infiltration | 4.219 | 4.1329 | 4.223 | 4.3161 | 4.16 | 4.3153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.207 | #N/A | #N/A | #N/A | 270-220 Cooling South Windows | #N/A | 6.6602 | 6.148 | 6.9116 | 6.7324 | 6.7908 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.7575 | #N/A | #N/A
97 | 240 Internal Gains | 2.431 | 2.6514 | 2.685 | 2.5071 | 2.605 | 2.6931 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.556 | #N/A | #N/A | #N/A | 280-270 Cooling Cavity Albedo | #N/A | -2.2745 | -2.483 | -2.3386 | -2.1028 | -2.4804 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.2697 | #N/A | #N/A
98 | 250 Exterior Solar Absorptance | 2.631 | 2.8371 | 2.855 | 2.6874 | 2.78 | 2.8744 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.719 | #N/A | #N/A | #N/A | 320-270 Cooling Thermostat | #N/A | -2.4123 | -2.278 | -2.5356 | -2.3955 | -2.5008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.4577 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 290-270 Cooling South Shading | #N/A | -1.6611 | -1.388 | -1.779 | -1.988 | -1.8273 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.6116 | #N/A | #N/A
99 | 270 South Windows | #N/A | 2.6114 | 2.56 | 2.5966 | 2.748 | 2.8432 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.668 | #N/A | #N/A | #N/A | 300-270 Cooling E&W Windows | #N/A | -2.2158 | -1.893 | -2.3695 | -2.2705 | -2.3755 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.2304 | #N/A | #N/A
100 | 280 Cavity Albedo | #N/A | 2.6122 | 2.568 | 2.602 | 2.752 | 2.8487 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.687 | #N/A | #N/A | #N/A | 310-300 Cooling E&W Shading | #N/A | -1.3032 | -1.403 | -1.4825 | -1.9102 | -1.5887 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.5437 | #N/A | #N/A
101 | 290 South Shading | #N/A | 2.6115 | 2.561 | 2.5834 | 2.75 | 2.8434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.67 | #N/A | #N/A | #N/A | PEAK HEATING [KW]
102 | 300 East/West Windows | #N/A | 2.6141 | 2.589 | 2.6031 | 2.766 | 2.8536 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.693 | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
103 | 310 East/West Shading | #N/A | 2.6149 | 2.592 | 2.5801 | 2.771 | 2.8563 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.7 | #N/A | #N/A | #N/A | 200-195 Heating Surface Convection | 0.47 | 0.43534 | 0.509 | 0.54692 | 0.473 | 0.5568 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.452 | #N/A | #N/A
104 | 320 Thermostat | #N/A | 2.609 | 2.546 | 2.5735 | 2.733 | 2.8335 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.642 | #N/A | #N/A | #N/A | CASES
105 | 395 Low Mass Solid Conduction | 1.948 | 2.1574 | 2.085 | 1.9517 | 2.09 | 2.1613 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.04 | #N/A | #N/A | #N/A | 210-200 Heating Ext IR (Int IR "off") | 0.102 | 0.40294 | 0.297 | 0.22323 | 0.396 | 0.39706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.319 | #N/A | #N/A
106 | 400 Low Mass High-Cond. Wall Elements | 2.559 | 2.8394 | 2.863 | 2.692 | 2.788 | 2.8786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.734 | #N/A | #N/A | #N/A | 220-215 Heating Ext IR (Int IR "on") | 0.11 | 0.41938 | 0.343 | 0.21421 | 0.398 | 0.3892 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.327 | #N/A | #N/A
107 | 410 Low Mass Infiltration | 3.338 | 3.4407 | 3.543 | 3.504 | 3.473 | 3.5969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.47 | #N/A | #N/A | #N/A | 220-210 Heating Int IR (Ext IR "on") | 0.257 | 0.2104 | 0.258 | 0.12747 | 0.117 | 0.12878 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.23 | #N/A | #N/A
108 | 420 Low Mass Internal Gains | 3.138 | 3.2562 | 3.365 | 3.3191 | 3.29 | 3.4115 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.292 | #N/A | #N/A | #N/A | 215-200 Heating Int IR (Ext IR "off") | 0.249 | 0.19396 | 0.212 | 0.13649 | 0.115 | 0.13665 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.222 | #N/A | #N/A
109 | 430 Low Mass Ext. Shortwave Absorptance | 3.3 | 3.2539 | 3.36 | 3.3163 | 3.285 | 3.4088 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.283 | #N/A | #N/A | #N/A
110 | 440 Low Mass Cavity Albedo | #N/A | 3.0272 | 3.06 | 3.2187 | 3.237 | 3.3743 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.227 | #N/A | #N/A | #N/A
111 | 450 Const. Int.&Ext. Surf. Coefs., Heating | 2.989 | 2.9783 | 2.753 | 3.0998 | 3.042 | 3.0373 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.036 | #N/A | #N/A | #N/A
112 | 460 Const. Interior Surf. Coefs., Heating | 3.055 | 2.9714 | 2.98 | 3.0911 | 3.101 | 3.1597 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.116 | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
113 | 470 Const. Exterior Surf. Coefs., Heating | 3.118 | 3.0007 | 2.807 | 3.2067 | 3.169 | 3.2315 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.112 | #N/A | #N/A | #N/A | 230-220 Heating Infiltration | 1.588 | 1.2935 | 1.36 | 1.6241 | 1.372 | 1.4367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.473 | #N/A | #N/A
114 | 800 High Mass High-Cond. Wall Elements | 2.957 | 2.7776 | 2.864 | 2.9237 | 2.84 | 2.9669 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.846 | #N/A | #N/A | #N/A | 240-220 Heating Internal Gains | -0.2 | -0.18795 | -0.178 | -0.18492 | -0.183 | -0.18548 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.178 | #N/A | #N/A
115 | 810 High Mass Cavity Albedo | #N/A | 2.5001 | 2.512 | 2.749 | 2.695 | 2.8447 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.727 | #N/A | #N/A | #N/A | 250-220 Heating Ext Solar Absorpance | 0 | -0.002311 | -0.008 | -0.0046183 | -0.008 | -0.0042134 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.015 | #N/A | #N/A
| ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS | [20 empty] | 270-220 Heating South Windows | #N/A | -0.228 | -0.303 | -0.09541 | -0.04 | -0.035333 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.066 | #N/A | #N/A
[22 empty] | 280-270 Heating Cavity Albedo | #N/A | 0.000866 | 0.008 | 0.005384 | 0.004 | 0.005441 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.019 | #N/A | #N/A
0 | COUNTRY: | [17 empty] | RANGE | RANGE |  | 320-270 Heating Thermostat | #N/A | -0.002429 | -0.014 | -0.023142 | -0.015 | -0.0097238 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.026 | #N/A | #N/A
KW | CASE# | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | MIN | MAX | AVERAGE | 290-270 Heating South Shading | #N/A | 7.1e-05 | 0.001 | -0.013189 | 0.002 | 0.00016606 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.002 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
105 | 395 Solid Conduction | 0.547 | 0.3575 | 0.308 | 0.37747 | 0.294 | 0.2652 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.282 | #N/A | #N/A | #N/A
109 | 430 High-Cond. Wall Elements | 2.167 | 1.8398 | 1.84 | 1.9294 | 1.874 | 1.7041 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.677 | #N/A | #N/A | #N/A | 215-210 | 0.147 | -0.20898 | -0.085 | -0.086742 | -0.281 | -0.26042 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.097 | #N/A | #N/A
70 | 600 South Windows | 5.65 | 6.481 | 5.422 | 6.3516 | 6.193 | 6.0457 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.609 | #N/A | #N/A | #N/A | 300-270 Heating E&W Windows | #N/A | 0.002675 | 0.029 | 0.0065091 | 0.018 | 0.010408 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.025 | #N/A | #N/A
71 | 610 S. Windows + Overhang | 5.466 | 6.4322 | 5.331 | 6.1345 | 5.934 | 5.8678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.344 | #N/A | #N/A | #N/A | 310-300 Heating E&W Shading | #N/A | 0.00082 | 0.003 | -0.023064 | 0.005 | 0.0026624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.007 | #N/A | #N/A
72 | 620 East & West Windows | 4.704 | 4.4928 | 3.955 | 4.7974 | 4.622 | 4.5883 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.236 | #N/A | #N/A | #N/A
73 | 630 E&W Windows + Overhang & Fins | 4.121 | 3.9983 | 3.526 | 4.2122 | 3.971 | 3.9494 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.631 | #N/A | #N/A | #N/A
74 | 640 Case 600 with Htg. Temp. Setback | 5.65 | 6.429 | 5.365 | 6.2974 | 6.127 | 5.9671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.495 | #N/A | #N/A | #N/A
75 | 650 Case 600 with Night Ventilation | 5.648 | 6.2897 | 5.045 | 6.1381 | 5.961 | 5.7975 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.441 | #N/A | #N/A | #N/A
New Cases 660 to 695 and 980 to 995
[19 empty] | MIN | MAX
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE
70 | 600 South Windows | 5.65 | 6.481 | 5.422 | 6.3516 | 6.193 | 6.0457 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.609 | #N/A | #N/A | #N/A
76 | 660 Low-E Windows | 3.343 | 3.933 | 3.355 | 3.7703 | 3.53 | 3.4574 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.435 | #N/A | #N/A | #N/A
77 | 670 Single-Pane Windows | 6.217 | 6.9253 | 5.839 | 6.8062 | 6.482 | 6.4013 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.941 | #N/A | #N/A | #N/A
78 | 680 Case 600 with Greater Insulation | 5.761 | 7.0513 | 5.861 | 6.7702 | 6.676 | 6.5566 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.028 | #N/A | #N/A | #N/A
79 | 685 Case 600 with 20/20 Tstat | 6.318 | 7.1594 | 6.071 | 7.1068 | 6.934 | 6.8674 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.288 | #N/A | #N/A | #N/A
80 | 695 Case 685 with Greater Insulation | 6.232 | 7.5407 | 6.355 | 7.3343 | 7.239 | 7.1752 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.618 | #N/A | #N/A | #N/A
81 | 900 South Windows | 3.039 | 3.3764 | 2.556 | 3.0404 | 2.896 | 2.9401 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.818 | #N/A | #N/A | #N/A
88 | 980 Case 900 with Greater Insulation | 3.384 | 3.668 | 2.93 | 3.4501 | 3.341 | 3.3126 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.157 | #N/A | #N/A | #N/A
89 | 985 Case 900 with 20/20 Tstat | 3.977 | 4.2253 | 3.208 | 3.9148 | 3.736 | 3.8847 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.516 | #N/A | #N/A | #N/A
90 | 995 Case 985 with Greater Insulation | 4.129 | 4.2238 | 3.315 | 4.1774 | 3.954 | 4.1149 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.643 | #N/A | #N/A | #N/A
PEAK COOLING [KW]
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
[22 empty] | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | DATA
[22 empty] | 200-195 Cooling Surface Convection | 0.153 | 0.22092 | 0.266 | 0.26648 | 0.254 | 0.26541 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.245 | #N/A | #N/A
[22 empty] | 210-200 Cooling Ext IR (Int IR "off") | -0.078 | -0.26955 | -0.302 | -0.22309 | -0.321 | -0.37477 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.313 | #N/A | #N/A
[22 empty] | 220-215 Cooling Ext IR (Int IR on) | -0.057 | -0.26079 | -0.346 | -0.2159 | -0.354 | -0.38409 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.327 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | [21 empty] | 0 | 0
114 | 800 High-Cond. Wall Elements | 1.286 | 1.1019 | 1.157 | 1.0458 | 1.052 | 0.93559 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.016 | #N/A | #N/A | #N/A | 215-200 Cooling Int IR (Ext IR "off") | 0.122 | 0.15407 | 0.147 | 0.092921 | 0.168 | 0.093176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.123 | #N/A | #N/A
81 | 900 South Windows | 3.039 | 3.3764 | 2.556 | 3.0404 | 2.896 | 2.9401 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.818 | #N/A | #N/A | #N/A | 220-210 Cooling Int IR (Ext IR "on") | 0.143 | 0.16283 | 0.103 | 0.1001 | 0.135 | 0.083849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.109 | #N/A | #N/A
82 | 910 S. Windows + Overhang | 2.493 | 2.7221 | 2.103 | 2.2221 | 2.212 | 2.081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.136 | #N/A | #N/A | #N/A | 230-220 Cooling Infiltration | 0.658 | 0.61968 | 0.694 | 0.6564 | 0.689 | 0.72555 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.714 | #N/A | #N/A
83 | 920 East & West Windows | 3.481 | 3.0567 | 2.71 | 3.2603 | 3.099 | 3.1541 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.909 | #N/A | #N/A | #N/A | 240-220 Cooling Internal Gains | 0.198 | 0.18623 | 0.178 | 0.18145 | 0.18 | 0.18157 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.177 | #N/A | #N/A
84 | 930 E&W Windows + Overhang & Fins | 3.052 | 2.6618 | 2.335 | 2.7815 | 2.494 | 2.6131 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.436 | #N/A | #N/A | #N/A | 250-220 Cooling Ext Solar Absorpance | 1.577 | 1.6815 | 1.711 | 1.6821 | 2.022 | 1.72 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.717 | #N/A | #N/A
85 | 940 Case 900 with Htg. Temp. Setback | 3.158 | 3.3764 | 2.556 | 3.04 | 2.891 | 2.9376 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.818 | #N/A | #N/A | #N/A | 270-220 Cooling South Windows | #N/A | 5.9025 | 4.792 | 5.6543 | 5.601 | 5.6695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.022 | #N/A | #N/A
86 | 950 Case 900 with Night Ventilation | 2.366 | 2.3635 | 2.054 | 2.3875 | 2.202 | 2.2364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.337 | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
87 | 960 Sunspace | #N/A | 1.3771 | 1.367 | 1.4799 | 1.403 | 1.3385 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.358 | #N/A | #N/A | #N/A | 280-270 Cavity Albedo | #N/A | -2.2459 | -2.064 | -2.1116 | -1.937 | -2.2376 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.875 | #N/A | #N/A
[22 empty] | 320-270 Thermostat | #N/A | -0.53772 | -0.528 | -0.62971 | -0.62 | -0.68806 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.604 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX | AVERAGE | 290-270 South Shading | #N/A | -0.13883 | -0.093 | -0.24426 | -0.202 | -0.23557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.249 | #N/A | #N/A
91 | 195 Solid Conduction | 1.118 | 0.99425 | 0.973 | 1.041 | 0.944 | 0.99351 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.977 | #N/A | #N/A | #N/A | 300-270 E&W Windows | #N/A | -2.8478 | -2.137 | -2.3633 | -2.392 | -2.3592 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.116 | #N/A | #N/A
92 | 200 Surface Convection Int IR="off" Ext IR="off" | 1.271 | 1.2152 | 1.239 | 1.3075 | 1.198 | 1.2589 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.222 | #N/A | #N/A | #N/A | 310-300 E&W Shading | #N/A | -0.36725 | -0.443 | -0.50594 | -0.603 | -0.57679 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.548 | #N/A | #N/A
93 | 210 Infrared Radiation Int IR="off" Ext IR="on" | 1.193 | 0.94562 | 0.937 | 1.0844 | 0.877 | 0.88416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.909 | #N/A | #N/A | #N/A
94 | 215 Infrared Radiation Int IR="on" Ext IR="off" | 1.393 | 1.3692 | 1.386 | 1.4004 | 1.366 | 1.3521 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.345 | #N/A | #N/A | #N/A | Low Mass REALISTIC DIAGNOSTIC TESTS
95 | 220 In-Depth Base Case | 1.336 | 1.1085 | 1.04 | 1.1845 | 1.012 | 0.96801 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.018 | #N/A | #N/A | #N/A | ANNUAL HEATING [MWH]
96 | 230 Infiltration | 1.994 | 1.7281 | 1.734 | 1.8409 | 1.701 | 1.6936 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.732 | #N/A | #N/A | #N/A
97 | 240 Internal Gains | 1.534 | 1.2947 | 1.218 | 1.3659 | 1.192 | 1.1496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.195 | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
98 | 250 Exterior Solar Absorptance | 2.913 | 2.79 | 2.751 | 2.8666 | 3.034 | 2.688 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.735 | #N/A | #N/A | #N/A | 400-395 Low Mass, Heating Surf. Conv. & IR | 1.341 | 1.6808 | 1.902 | 1.7066 | 1.7443 | 1.8611 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.8521 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX | AVERAGE | 410-400 Low Mass, Heating Infiltration | 1.724 | 1.5093 | 1.614 | 1.7325 | 1.6022 | 1.6757 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.6881 | #N/A | #N/A
99 | 270 South Windows | #N/A | 7.011 | 5.832 | 6.8388 | 6.613 | 6.6375 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.04 | #N/A | #N/A | #N/A | 420-410 Low Mass, Heating Int. Gains | -1.231 | -1.2106 | -1.228 | -1.1745 | -1.1852 | -1.2086 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2169 | #N/A | #N/A
100 | 280 Cavity Albedo | #N/A | 4.7651 | 3.768 | 4.7272 | 4.676 | 4.3999 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.165 | #N/A | #N/A | #N/A | 600-430 Low Mass, Heating S. Window | -1.121 | -1.4613 | -1.907 | -1.2958 | -1.1829 | -1.347 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4692 | #N/A | #N/A
101 | 290 South Shading | #N/A | 6.8722 | 5.739 | 6.5946 | 6.411 | 6.4019 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.791 | #N/A | #N/A | #N/A | 430-420 Low Mass, Heating Ext. Solar Abs. | -1.228 | -1.3804 | -1.479 | -1.2857 | -1.4821 | -1.3858 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4093 | #N/A | #N/A
102 | 300 East/West Windows | #N/A | 4.1631 | 3.695 | 4.4755 | 4.221 | 4.2782 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.924 | #N/A | #N/A | #N/A | 440-600 Low Mass, Heating Cavity Albedo | #N/A | 0.16318 | 0.283 | 0.17569 | 0.1419 | 0.21713 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2533 | #N/A | #N/A
103 | 310 East/West Shading | #N/A | 3.7959 | 3.252 | 3.9695 | 3.618 | 3.7015 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.376 | #N/A | #N/A | #N/A | ANNUAL COOLING [MWH]
104 | 320 Thermostat | #N/A | 6.4733 | 5.304 | 6.2091 | 5.993 | 5.9494 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.436 | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
105 | 395 Low Mass Solid Conduction | 0.547 | 0.3575 | 0.308 | 0.37747 | 0.294 | 0.2652 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.282 | #N/A | #N/A | #N/A | CASES | [16 empty] | 0
106 | 400 Low Mass High-Cond. Wall Elements | 0.798 | 0.49365 | 0.457 | 0.60691 | 0.456 | 0.37199 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.445 | #N/A | #N/A | #N/A | 400-395 Low Mass, Cooling Surf. Conv. & IR | 0.042 | 0.015542 | 0.011 | 0.020185 | 0.0189 | 0.0091667 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0104 | #N/A | #N/A
107 | 410 Low Mass Infiltration | 1.011 | 0.69988 | 0.709 | 0.82785 | 0.624 | 0.60368 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.691 | #N/A | #N/A | #N/A | 410-400 Low Mass, Cooling Infiltration | 0.033 | 0.025188 | 0.024 | 0.026703 | 0.0279 | 0.022437 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0244 | #N/A | #N/A
108 | 420 Low Mass Internal Gains | 1.208 | 0.90853 | 0.917 | 1.0325 | 0.836 | 0.81407 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.886 | #N/A | #N/A | #N/A
109 | 430 Low Mass Ext. Shortwave Absorptance | 2.167 | 1.8398 | 1.84 | 1.9294 | 1.874 | 1.7041 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.677 | #N/A | #N/A | #N/A
110 | 440 Low Mass Cavity Albedo | #N/A | 4.6655 | 3.766 | 4.686 | 4.679 | 4.3076 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.184 | #N/A | #N/A | #N/A | 215-200 | 0.113 | 0.14556 | 0.087 | 0.063388 | 0.0944 | 0.062024 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0878 | #N/A | #N/A
111 | 450 Const. Int.&Ext. Surf. Coefs., Cooling | 5.812 | 6.1798 | 6.063 | 6.4663 | 6.501 | 6.3134 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.399 | #N/A | #N/A | #N/A
112 | 460 Const. Interior Surf. Coefs., Cooling | 5.804 | 6.2429 | 5.902 | 6.3742 | 6.304 | 6.0689 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.152 | #N/A | #N/A | #N/A
113 | 470 Const. Exterior Surf. Coefs., Cooling | 5.695 | 6.3877 | 5.57 | 6.4436 | 6.407 | 6.32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.768 | #N/A | #N/A | #N/A
114 | 800 High Mass High-Cond. Wall Elements | 1.286 | 1.1019 | 1.157 | 1.0458 | 1.052 | 0.93559 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.016 | #N/A | #N/A | #N/A | 420-410 Low Mass, Cooling Int. Gains | 0.132 | 0.092126 | 0.078 | 0.095302 | 0.0896 | 0.074316 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0774 | #N/A | #N/A
115 | 810 High Mass Cavity Albedo | #N/A | 2.4105 | 1.94 | 2.2702 | 2.179 | 2.1129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.233 | #N/A | #N/A | #N/A | 430-420 Low Mass, Cooling Ext Solar Abs. | 0.856 | 0.76554 | 0.825 | 0.70305 | 0.8108 | 0.62959 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.6331 | #N/A | #N/A
| FREE-FLOAT TEMPERATURE OUTPUT | [20 empty] | 600-430 Low Mass, Cooling S. Window | 4.738 | 5.007 | 4.488 | 5.1714 | 5.2091 | 5.0405 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.0397 | #N/A | #N/A
| MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [20 empty] | 440-600 Low Mass, Cooling Cavity Albedo | #N/A | -1.9278 | -1.974 | -1.942 | -1.7477 | -2.0384 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8663 | #N/A | #N/A
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | PEAK HEATING [KW] --Charts not created directly here; these addresses are referenced by "BESTEST IN-DEPTH CASES 395 TO 600 DELTA CHART - ANNUAL" below
0 | COUNTRY:
TMP (C) | CASE# | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C)
[19 empty] | MIN | MAX | AVERAGE |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
130 | 600FF - Low Mass Building with South Windows | 63.4 | 68.3608 | 65 | 63.8408 | 64.6 | 62.3692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 64.46 | #N/A | #N/A | #N/A | 400-395 Low Mass, Heating Surf. Conv. & IR | 0.611 | 0.68193 | 0.778 | 0.74028 | 0.698 | 0.71723 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.694 | #N/A | #N/A
131 | 900FF - High Mass Building with South Windows | 46 | 45.1138 | 44.46 | 44.2922 | 44.3 | 43.2522 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44.84 | #N/A | #N/A | #N/A | 410-400 Low Mass, Heating Infiltration | 0.779 | 0.60131 | 0.68 | 0.81203 | 0.685 | 0.71836 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.736 | #N/A | #N/A
132 | 650FF Case 600FF with Night Ventilation | 62.1 | 66.8465 | 62.59 | 62.469 | 63.3 | 61.1332 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 62.99 | #N/A | #N/A | #N/A | 215-200 | 0.249 | 0.19396 | 0.212 | 0.13649 | 0.115 | 0.13665 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.222 | #N/A | #N/A
133 | 950FF Case 900FF with Night Ventilation | 37.1 | 36.7765 | 36.37 | 36.6805 | 36.4 | 36.1267 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 37.33 | #N/A | #N/A | #N/A | 420-410 Low Mass, Heating Int. Gains | -0.2 | -0.18445 | -0.178 | -0.18492 | -0.183 | -0.18548 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.178 | #N/A | #N/A
134 | 680FF Case 600FF with More Insulation | 72.5 | 78.5143 | 74.97 | 70.1447 | 72.2 | 69.7742 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 72.36 | #N/A | #N/A | #N/A | 430-420 Low Mass, Heating Ext Solar Abs. | 0.162 | -0.002354 | -0.005 | -0.002869 | -0.005 | -0.0026383 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.009 | #N/A | #N/A
135 | 980FF Case 900FF with More Insulation | 49.7 | 52.2464 | 52.81 | 49.6221 | 50.2 | 48.5406 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 51.03 | #N/A | #N/A | #N/A | 600-430 Low Mass, Heating S. Window | -0.045 | -0.23365 | -0.325 | -0.11183 | -0.057 | -0.049923 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.085 | #N/A | #N/A
136 | 960 Sunspace | #N/A | 48.9033 | 53.18 | 49.8773 | 49.5 | 48.0966 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 440-600 Low Mass, Heating Cavity Albedo | #N/A | 0.006973 | 0.025 | 0.014228 | 0.009 | 0.015399 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.029 | #N/A | #N/A
MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | PEAK COOLING [KW]
0 | COUNTRY: | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
TMP (C) | CASE# | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) |  |  |  | CASES
[22 empty] | 400-395 Low Mass, Cooling Surf. Conv. & IR | 0.251 | 0.13615 | 0.149 | 0.22943 | 0.162 | 0.10678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.163 | #N/A | #N/A
[19 empty] | MIN | MAX | AVERAGE | 410-400 Low Mass, Cooling Infiltration | 0.213 | 0.20623 | 0.252 | 0.22094 | 0.168 | 0.2317 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.246 | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 420-410 Low Mass, Cooling Int. Gains | 0.197 | 0.20865 | 0.208 | 0.20469 | 0.212 | 0.21039 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.195 | #N/A | #N/A
130 | 600FF - Low Mass Building with South Windows | -9.9 | -12.8904 | -13.52 | -12.5613 | -13.5 | -13.8442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -13.79 | #N/A | #N/A | #N/A | 430-420 Low Mass, Cooling Ext. Solar Abs. | 0.959 | 0.93129 | 0.923 | 0.89683 | 1.038 | 0.89001 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.791 | #N/A | #N/A
131 | 900FF - High Mass Building with South Windows | 0.6 | 2.1647 | 1.31 | 1.2424 | 1.6 | 0.63931 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8 | #N/A | #N/A | #N/A | 600-430 Low Mass, Cooling S. Window | 3.483 | 4.6412 | 3.582 | 4.4222 | 4.319 | 4.3417 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.932 | #N/A | #N/A
132 | 650FF Case 600FF with Night Ventilation | -16.7 | -17.7616 | -17.37 | -17.0758 | -17.5 | -17.5067 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -17.47 | #N/A | #N/A | #N/A | 440-600 Low Mass, Cooling Cavity Albedo | #N/A | -1.8155 | -1.656 | -1.6656 | -1.514 | -1.7382 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.425 | #N/A | #N/A
133 | 950FF Case 900FF with Night Ventilation | -13.2 | -13.2443 | -13.36 | -12.8122 | -12.5 | -12.7995 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -13.42 | #N/A | #N/A | #N/A
134 | 680FF Case 600FF with More Insulation | -5.7 | -6.1966 | -6.89 | -7.0523 | -7.2 | -8.0736 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -8.01 | #N/A | #N/A | #N/A
135 | 980FF Case 900FF with More Insulation | 7.3 | 12.5361 | 12.4 | 9.917 | 10.5 | 9.4717 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10.44 | #N/A | #N/A | #N/A
136 | 960 Sunspace | #N/A | 8.0165 | 6.74 | 5.0931 | 5 | 4.2376 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | High Mass DIAGNOSTIC TESTS
| AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C) | [20 empty] | ANNUAL HEATING [MWH]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | [20 empty] | CASES
TMP (C) | CASE# | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) |  |  |  | 800-430 Mass, Heating w/ High Cond. Wall El. | -0.03 | -0.54834 | -0.551 | -0.50457 | -0.5651 | -0.48107 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4966 | #N/A | #N/A
130 | 600FF - Low Mass Building with South Windows | 26.1 | 25.5736 | 25.26 | 24.9173 | 25.26 | 24.2578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.8 | #N/A | #N/A | #N/A | 900-800 High Mass, Heating S. Window | -3.415 | -3.5268 | -3.812 | -3.4519 | -3.3951 | -3.5554 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.6636 | #N/A | #N/A
131 | 900FF - High Mass Building with South Windows | 25.5 | 25.6921 | 25.25 | 25.1213 | 25.34 | 24.4623 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.93 | #N/A | #N/A | #N/A | 900-810 High Mass, Heating Int. Sol. Abs. | #N/A | -0.65862 | -0.863 | -0.67814 | -0.6003 | -0.79572 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.7783 | #N/A | #N/A
132 | 650FF Case 600FF with Night Ventilation | 17.6 | 18.4599 | 18.04 | 18.4195 | 18.93 | 18.402 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.71 | #N/A | #N/A | #N/A | 910-610 Mass, Heating w/ S. Shade | -2 | -2.4187 | -2.284 | -2.4191 | -2.4598 | -2.4603 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.4704 | #N/A | #N/A
133 | 950FF Case 900FF with Night Ventilation | 15 | 14.7096 | 14.35 | 14.789 | 14.78 | 14.6786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 14.77 | #N/A | #N/A | #N/A | 920-620 Mass, Heating w/ E&W Window | -0.87 | -1.1375 | -1.038 | -1.1486 | -1.2146 | -1.1123 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1468 | #N/A | #N/A
134 | 680FF Case 600FF with More Insulation | 31.8 | 33.1103 | 33.3 | 30.9584 | 31.71 | 30.1869 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 31.4 | #N/A | #N/A | #N/A | 930-630 Mass, Heating w/ E&W Shade | -0.653 | -0.8323 | -0.744 | -0.78974 | -0.773 | -0.75448 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.791 | #N/A | #N/A
135 | 980FF Case 900FF with More Insulation | 30.7 | 33.2952 | 33.3 | 31.1618 | 31.84 | 30.492 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 31.56 | #N/A | #N/A | #N/A | 940-640 Mass, Heating w/ Heating Setback | -1.293 | -1.54 | -1.47 | -1.5945 | -1.6397 | -1.4836 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.3618 | #N/A | #N/A
136 | 960 Sunspace | #N/A | 28.5573 | 29.45 | 27.7427 | 27.74 | 26.7976 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
SOLAR RADIATION
| ANNUAL INCIDENT TOTAL | [20 empty] | ANNUAL COOLING [MWH]
| CASE 600 | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
CASES
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 800-430 Mass, Cooling w/ High Cond. Wall El. | -0.611 | -0.52633 | -0.582 | -0.48209 | -0.5613 | -0.45694 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4819 | #N/A | #N/A
0 | = | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 900-800 High Mass, Cooling S. Window | 2.241 | 2.084 | 2.021 | 2.1152 | 2.0963 | 1.985 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.1924 | #N/A | #N/A
155 | 600 HORZ. | 1670 | 1662.5278 | 1667.158 | 1664.3425 | 1665.18 | 1668.98 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1663.67 |  |  |  | 900-810 High Mass, Cooling Int. Sol. Abs. | #N/A | 0.98312 | 1.026 | 0.98095 | 0.8821 | 0.97261 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9952 | #N/A | #N/A
156 | 600 NORTH | 453 | 399.0475 | 477.31 | 438.241 | 432.12 | 440.165 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 432.25 | #N/A | #N/A | #N/A | 910-610 Mass, Cooling w/ S. Shade | -2.815 | -2.9669 | -2.683 | -2.9493 | -2.9496 | -2.9259 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.8623 | #N/A | #N/A
157 | 600 EAST | 1061 | 1026.9874 | 1016.676 | 1062.1572 | 1054.24 | 1067.94 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1061 | #N/A | #N/A | #N/A | 920-620 Mass, Cooling w/ E&W Window | -1.276 | -1.2901 | -1.203 | -1.3287 | -1.4313 | -1.2918 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.274 | #N/A | #N/A
158 | 600 SOUTH | 1387 | 1316.9162 | 1290.593 | 1370.4819 | 1363.1 | 1384.23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1381.75 | #N/A | #N/A | #N/A | 930-630 Mass, Cooling w/ E&W Shade | -0.913 | -0.94541 | -0.879 | -0.91693 | -0.9415 | -0.90111 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.91 | #N/A | #N/A
159 | 600 WEST | 997 | 903.0665 | 905.722 | 967.278 | 961.18 | 974.473 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 968.92 | #N/A | #N/A | #N/A | 940-640 Mass, Cooling w/ Heating Setback | -3.191 | -3.2473 | -2.894 | -3.3387 | -3.465 | -3.2738 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.034 | #N/A | #N/A
[22 empty] | 950-650 Mass, Cooling w/ Night Vent | -4.043 | -4.0559 | -3.568 | -4.1099 | -4.2891 | -3.9907 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.8775 | #N/A | #N/A
[22 empty] | PEAK HEATING [KW] | [17 empty] | 0 | 0
| = | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
CASES
| SOLAR RADIATION | [20 empty] | 800-430 Mass, Heating w/ High Cond. Wall El. | -0.343 | -0.47625 | -0.496 | -0.3926 | -0.445 | -0.44187 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.437 | #N/A | #N/A
| UNSHADED ANNUAL TRANSMITTED | [20 empty] | 900-800 High Mass, Heating S. Window | -0.406 | -0.33425 | -0.411 | -0.23616 | -0.207 | -0.18847 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.174 | #N/A | #N/A
[22 empty] | 900-810 High Mass, Heating Int. Sol. Abs. | #N/A | -0.056746 | -0.059 | -0.061545 | -0.062 | -0.066177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.055 | #N/A | #N/A
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 910-610 Mass, Heating w/ S. Shade | -0.405 | -0.55173 | -0.565 | -0.49292 | -0.549 | -0.56031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.51 | #N/A | #N/A
0 | COUNTRY: | [20 empty] | 920-620 Mass, Heating w/ E&W Window | -0.25 | -0.52543 | -0.555 | -0.45894 | -0.547 | -0.52032 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5 | #N/A | #N/A
kWh/m2 | CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | MIN | MAX |  | 930-630 Mass, Heating w/ E&W Shade | -0.284 | -0.5024 | -0.523 | -0.42166 | -0.494 | -0.48714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.473 | #N/A | #N/A
0 | = | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 940-640 Mass, Heating w/ Heating Setback | -0.751 | -1.1705 | -0.999 | -1.4158 | -0.979 | -0.63372 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.821 | #N/A | #N/A
163 | 600 SOUTH | 820 | 825.5194 | 805.046 | 804.0205 | 813.88 | 822.589 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 803.14 | #N/A | #N/A | #N/A
166 | 620 WEST | 598 | #N/A | 569.394 | 581.0395 | 591.88 | 623.797 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 635.14 | #N/A | #N/A | #N/A
164 | 660 SOUTH, Low-E | 447 | 501.3136 | 506.461 | 435.995 | 442.7 | 448.493 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 443.78
165 | 670 SOUTH, Single Pane | 1037 | 987.8182 | 994.318 | 1024.2026 | 1028.35 | 1039.23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1037.54
PEAK COOLING [KW] --Charts not created directly here; these addresses are referenced by "BASIC AND IN-DEPTH MASS EFFECT DELTA CHART - PEAK" below
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
CASES
[22 empty] | 800-430 Mass, Cooling w/ High Cond. Wall El. | -0.881 | -0.73794 | -0.683 | -0.88353 | -0.822 | -0.76849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.661 | #N/A | #N/A
| SOLAR RADIATION | [20 empty] | 900-800 High Mass, Cooling S. Window | 1.753 | 2.2746 | 1.399 | 1.9946 | 1.844 | 2.0045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.802 | #N/A | #N/A
| SHADED ANNUAL TRANSMITTED | [20 empty] | 900-810 High Mass, Cooling Int. Sol. Abs. | #N/A | 0.96595 | 0.616 | 0.77023 | 0.717 | 0.8272 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.585 | #N/A | #N/A
[22 empty] | 910-610 Mass, Cooling w/ S. Shade | -2.973 | -3.7101 | -3.228 | -3.9124 | -3.722 | -3.7868 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.208 | #N/A | #N/A
| CODENAME: | [20 empty] | 920-620 Mass, Cooling w/ E&W Window | -1.223 | -1.4361 | -1.245 | -1.5371 | -1.523 | -1.4341 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.327 | #N/A | #N/A
| COUNTRY: | [20 empty] | 930-630 Mass, Cooling w/ E&W Shade | -1.069 | -1.3365 | -1.191 | -1.4307 | -1.477 | -1.3363 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.195 | #N/A | #N/A
kWh/m2 | CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | MIN | MAX |  | 940-640 Mass, Cooling w/ Heating Setback | -2.492 | -3.0526 | -2.809 | -3.2574 | -3.236 | -3.0295 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.677 | #N/A | #N/A
0 | = | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 950-650 Mass, Cooling w/ Night Vent | -3.282 | -3.9262 | -2.991 | -3.7506 | -3.759 | -3.5611 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.104 | #N/A | #N/A
170 | 610 SOUTH | 641 | 665.2609 | 663.345 | 646.1319 | 631.33 | 661.81 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 662.39 | #N/A | #N/A | #N/A
171 | 630 WEST | 438 | #N/A | 399.173 | 419.3545 | 389.67 | 445.549 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 464.21 | #N/A | #N/A | #N/A
SOLAR RADIATION
ANNUAL TRANSMISSIVITY COEFFICIENT OF WINDOWS
CODENAME:
COUNTRY:
| CASE# | [17 empty] | MIN | MAX
0 | = | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
math | 600 SOUTH | 0.5912 | 0.62686 | 0.62378 | 0.58667 | 0.59708 | 0.59426 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.58125 | #N/A | #N/A | #N/A
math | 620 WEST | 0.5998 | #N/A | 0.62866 | 0.6007 | 0.61578 | 0.64014 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.65551 | #N/A | #N/A | #N/A
math | 660 SOUTH, Low-E | 0.32228 | 0.38067 | 0.39243 | 0.31813 | 0.32477 | 0.324 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.32117 | #N/A | #N/A | #N/A
math | 670 SOUTH, Single Pane | 0.74766 | 0.7501 | 0.77043 | 0.74733 | 0.75442 | 0.75076 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.75089 | #N/A | #N/A | #N/A
SOLAR RADIATION
ANNUAL OVERHANG AND FIN SHADING COEFFICIENT
CODENAME:
COUNTRY:
| CASE# | [17 empty] | MIN | MAX
0 | test | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
math | (1 - Case610 / Case600) SOUTH | 0.21829 | 0.19413 | 0.17602 | 0.19637 | 0.2243 | 0.19545 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.17525
math | (1 - Case630 / Case620) WEST | 0.26756 | #N/A | 0.29895 | 0.27827 | 0.34164 | 0.28575 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.26912
SKY TEMPERATURE, CASE 600
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
178 | Average | #N/A | -3.9307 | -5.9 | -2.0216 | -5.17 | -5.0587 | -5.9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -5.27
178 | Minimum | #N/A | -46.2246 | -46.85 | -37.9798 | -46.9 | -46.1617 | -46.85 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -46.97
178 | Maximum | #N/A | 30.0812 | 24.62 | 24.7268 | 26.7 | 26.0293 | 24.62 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27.28
[22 empty] | NOT USED TO GENERATE CHARTS |  |  |  |  | NOT USED TO GENERATE CHARTS |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS
[34 empty] | SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
[22 empty] | ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS | [11 empty] | USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA |  | RANGE | RANGE
[22 empty] | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | MIN | MAX
[22 empty] | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | JAN 04 | 2 | 4.307 | 1904-01-01 | 2 | 4.037 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.354 | JAN 04 | 2 |  |  |  | 3.437 | 4.354
[22 empty] | CASE# | KW | DATE | HR | HR | KW | DATE | HR | KW | DATE | HR | KW | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.037 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.354 | JAN 04 | 2 |  |  |  | 3.437 | 4.354
[22 empty] | 600 | 3.437 | 1993-01-04 | 5 | 5 | 3.94 | JAN 04 | 5 | 4.045 | JAN 04 | 5 | 4.258 | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.277 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.379 | JAN 04 | 2 |  |  |  | 3.591 | 4.379
[22 empty] | 610 | 3.437 | 1993-01-04 | 5 | 5 | 3.941 | JAN 04 | 5 | 4.034 | JAN 04 | 5 | 4.258 | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.278 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.379 | JAN 04 | 2 |  |  |  | 3.592 | 4.278
[22 empty] | 620 | 3.591 | 1993-01-04 | 6 | 6 | 3.941 | JAN 04 | 5 | 4.046 | JAN 04 | 5 | 4.277 | JAN 04 | 8 | 8.078 | 1904-01-01 | 8 | 6.347 | JAN 04 | 8 | 5.7222 | Jan-04 | 8 | 6.954 | JAN 04 | 8 |  |  |  | 5.232 | 6.954
[22 empty] | 630 | 3.592 | 1993-01-04 | 7 | 7 | 3.941 | JAN 04 | 5 | 4.025 | JAN 04 | 5 | 4.28 | USA KW: 0; UK-BRE KW: 0; SPAIN KW: 0; BEL/UK KW: 0
[22 empty] | 640 | 5.232 | 1993-01-04 | 7 | 7 | 5.486 | JAN 04 | 8 | 5.943 | JAN 04 | 8 | 6.53 | JAN 04 | 7 | 4.081 | 1904-01-01 | 7 | 3.608 | JAN 04 | 8 | 3.5167 | Jan-04 | 7 | 3.797 | JAN 04 | 7 |  |  |  | 2.85 | 3.797
[22 empty] | 650 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 | JAN 04 | 7 | 4.083 | 1904-01-01 | 7 | 3.618 | JAN 04 | 8 | 3.5361 | Jan-04 | 7 | 3.801 | JAN 04 | 7 |  |  |  | 2.858 | 3.801
[22 empty] | 900 | 2.85 | 1993-01-04 | 7 | 7 | 3.453 | JAN 04 | 7 | 3.557 | JAN 04 | 7 | 3.76 | JAN 04 | 7 | 4.156 | 1904-01-01 | 7 | 4.029 | JAN 04 | 7 | 3.7083 | Jan-04 | 7 | 4.061 | JAN 04 | 7 |  |  |  | 3.308 | 4.061
[22 empty] | 910 | 2.858 | 1993-01-04 | 7 | 7 | 3.456 | JAN 04 | 7 | 3.564 | JAN 04 | 7 | 3.764 | JAN 04 | 7 | 4.165 | 1904-01-01 | 7 | 4.064 | JAN 04 | 7 | 3.7444 | Jan-04 | 7 | 4.188 | JAN 04 | 8 |  |  |  | 3.355 | 4.064
[22 empty] | 920 | 3.308 | 1993-01-04 | 7 | 7 | 3.703 | JAN 04 | 7 | 3.805 | JAN 04 | 7 | 4.013 | JAN 04 | 8 | 9.923 | 1904-01-01 | 8 | 6.117 | JAN 04 | 8 | 5.1222 | Jan-03 | 9 | 6.428 | JAN 04 | 8 |  |  |  | 3.98 | 6.428
[22 empty] | 930 | 3.355 | 1993-01-04 | 7 | 7 | 3.732 | JAN 04 | 7 | 3.832 | JAN 04 | 7 | 4.042 | USA KW: 0; UK-BRE KW: 0; SPAIN KW: 0; BEL/UK KW: 0
| HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MAY 4 | [20 empty] | 940 | 3.98 | 1993-01-04 | 7 | 7 | 5.028 | JAN 04 | 8 | 5.665 | JAN 04 | 8 | 6.116 | JAN 04 | 8 | 2.896 | 1904-01-01 | 8 | 2.852 | JAN 04 | 8 | 2.522 | Jan-04 | 8 | 2.779 | JAN 04 | 8 |  |  |  | 2.41 | 2.896
| CASE 600 OR 900 | [20 empty] | 950 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 | USA DATE: JAN 04; USA HR: 7; USA KW: 3.738; UK-BRE DATE: Feb-06; UK-BRE HR: 2; UK-BRE KW: 3.799; SPAIN DATE: JAN 04; SPAIN HR: 8; BEL/UK KW: 4.296; FINLAND DATE: JAN 04; FINLAND HR: 7
| SOUTH SURFACE | [20 empty] | 960 | 2.41 | 1993-01-04 | 7 | 7 | 2.751 | JAN 04 | 8 | 2.727 | JAN 04 | 8 | 2.863 | JAN 04 | 3 | 2.235 | 1904-01-01 | 3 | 2.221 | JAN 04 | 4 | 2.1856 | Jan-04 | 3 | 2.263 | JAN 04 | 3
| (USE COLUMN B ONLY) | [20 empty] | 990 | 2.769 | 1993-02-06 | 2 | 2 | 3.734 | JAN 04 | 7 | 3.427 | JAN 04 | 7 | 3.681 |  |  | 3.047 | 1904-01-01 | 3 | 2.999 | JAN 04 | 2 | 2.9694 | Jan-04 | 5 | 3.382 | JAN 04 | 2
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 195 | 2.004 | 1993-01-04 | 2 | 2 | 2.186 | JAN 04 | 8 | 2.32 | JAN 04 | 3 | 2.385 |  |  | 3.077 | 1904-01-01 | 3 | 3.02 | JAN 04 | 2 | 2.9806 | Jan-04 | 5 | 3.325 | JAN 04 | 2
0 | COUNTRY: | [20 empty] | 200 | 2.651 | 1993-01-04 | 5 | 5 | 2.973 | JAN 04 | 5 | [6 empty] | 3.65 | 1904-01-01 | 2 | 3.307 | JAN 04 | 6 | 3.2944 | Jan-04 | 6 | 3.458 | JAN 04 | 8
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 210 | 2.701 | 1993-01-04 | 5 | 5 | 2.973 | JAN 04 | 5 |  |  |  |  | JAN 04 | 2 | 3.709 | 1904-01-01 | 2 | 3.348 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 215 | 2.787 | 1993-01-04 | 5 | 5 | 3.28 | JAN 04 | 5 |  |  |  |  | JAN 04 | 2 | 5.293 | 1904-01-01 | 2 | 5.159 | JAN 04 | 2 | 4.8917 | Jan-04 | 6 | 5.107 | JAN 04 | 2
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 220 | 2.867 | 1993-01-04 | 5 | 5 | 3.28 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 | 3.509 | 1904-01-01 | 2 | 3.159 | JAN 04 | 8 | 3.1528 | Jan-04 | 6 | 3.333 | JAN 04 | 8
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 230 | 4.386 | 1993-01-04 | 5 | 5 | 4.984 | JAN 04 | 2 | 4.994 | JAN 04 | 2 | 5.279 | JAN 04 | 2 | 3.709 | 1904-01-01 | 2 | 3.341 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.525 | JAN 04 | 2
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 240 | 2.685 | 1993-01-04 | 5 | 5 | 3.1 | JAN 04 | 5 | 3.282 | JAN 04 | 5 | 3.495 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.34 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.738 | JAN 04 | 2
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 250 | 2.866 | 1993-01-04 | 5 | 5 | 3.279 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.341 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.759 | JAN 04 | 2
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 270 | 2.863 | 1993-01-04 | 5 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.67 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.34 | JAN 04 | 6 | 3.3278 | Jan-04 | 6 | 3.738 | JAN 04 | 2
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 280 | 2.864 | 1993-01-04 | 5 | 5 | 3.278 | JAN 04 | 5 |  |  |  | 3.685 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.599 | JAN 04 | 5 | 3.3278 | Jan-04 | 6 | 3.77 | JAN 04 | 2
235 | 6 | 9.31 | 9.0004 | 9 | 10.9831 | 9.22 | 7.7154 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.74 |  |  |  | 290 | 2.863 | 1993-01-04 | 5 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.67 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.599 | JAN 04 | 5 | 3.3278 | Jan-04 | 6 | 3.771 | JAN 04 | 2
236 | 7 | 36.36 | 36.0015 | 36 | 33.8229 | 31.59 | 31.2881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 31.29 |  |  |  | 300 | 3.014 | 1993-01-04 | 6 | 6 | 3.276 | JAN 04 | 5 |  |  |  | 3.685 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.34 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.735 | JAN 04 | 3
237 | 8 | 66.16 | 66.6028 | 66.6 | 59.9654 | 57.22 | 58.0581 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 57.48 |  |  |  | 310 | 3.015 | 1993-01-04 | 6 | 6 | 3.277 | JAN 04 | 5 |  |  |  | 3.672 | JAN 04 | 3 | 2.391 | 1904-01-01 | 3 | 2.263 | JAN 04 | 4 | 2.2211 | Jan-04 | 8 | 2.27 | JAN 04 | 3
238 | 9 | 93.88 | 94.8038 | 94.8 | 84.3926 | 82.11 | 83.1431 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 82.85 |  |  |  | 320 | 2.861 | 1993-01-04 | 5 | 5 | 3.275 | JAN 04 | 5 |  |  |  | 3.661 | JAN 04 | 2 | 3.709 | 1904-01-01 | 2 | 3.342 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2
239 | 10 | 116.03 | 117.0048 | 117 | 108.1146 | 105.56 | 103.6598 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 103.65 |  |  |  | 395 | 2.062 | 1993-01-04 | 7 | 7 | 2.209 | JAN 04 | 8 | 2.328 | JAN 04 | 3 | 2.385 | JAN 04 | 2 | 4.501 | 1904-01-01 | 2 | 4.227 | JAN 04 | 2 | 4.1139 | Jan-04 | 6 | 4.314 | JAN 04 | 2
240 | 11 | 156.44 | 157.8065 | 157.8 | 139.6057 | 137.73 | 141.3514 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 141.61 |  |  |  | 400 | 2.867 | 1993-01-04 | 5 | 5 | 3.28 | JAN 04 | 5 | 3.476 | JAN 04 | 5 | 3.695 | JAN 04 | 2 | 4.301 | 1904-01-01 | 2 | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.126 | JAN 04 | 2
241 | 12 | 165.66 | 166.8069 | 166.8 | 149.4359 | 149.3 | 150.3411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 150.74 |  |  |  | 410 | 3.625 | 1993-01-04 | 5 | 5 | 4.124 | JAN 04 | 5 | 4.233 | JAN 04 | 5 | 4.487 | JAN 04 | 2 | 4.301 | 1904-01-01 | 2 | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.137 | JAN 04 | 2
242 | 13 | 165.04 | 166.2068 | 166.2 | 147.9223 | 148.6 | 149.7167 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 150.11 |  |  |  | 420 | 3.443 | 1993-01-04 | 5 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.041 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.376 | JAN 04 | 2
243 | 14 | 154 | 155.4066 | 155.4 | 136.7123 | 137.97 | 138.9957 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 139.22
244 | 15 | 134.48 | 136.2054 | 136.2 | 117.6082 | 119.2 | 120.4472 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 120.37 |  |  |  | 430 | 3.442 | 1993-01-04 | 5 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 | 4.188 | 1904-01-01 | 8 | 3.902 | JAN 04 | 8 | 3.7861 | Jan-04 | 7 | 3.939 | JAN 04 | 7
245 | 16 | 106.77 | 108.6046 | 108.6 | 90.0007 | 92.17 | 94.7457 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 94.26 |  |  |  | 440 | 3.439 | 1993-01-04 | 5 | 5 | 3.942 | JAN 04 | 5 |  |  |  | 4.277 | JAN 04 | 7 | 4.115 | 1904-01-01 | 7 | 3.709 | JAN 04 | 8 | 3.6056 | Jan-04 | 7 | 3.963 | JAN 04 | 7
246 | 17 | 62.05 | 62.4026 | 62.4 | 53.2617 | 55.39 | 54.3851 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 53.76 |  |  |  | 800 | 3.227 | 1993-01-04 | 5 | 5 | 3.793 | JAN 04 | 7 | 3.909 | JAN 04 | 7 | 4.138
247 | 18 | 32.2 | 31.8013 | 31.8 | 26.165 | 28.16 | 27.594 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27.69 |  |  |  | 810 | 2.979 | 1993-01-04 | 7 | 7 | 3.566 | JAN 04 | 7 |  |  |  | 3.915 | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
248 | 19 | 6.81 | 6.6003 | 6.6 | 5.4293 | 7.34 | 5.6434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.66 |  |  |  | ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA; RANGE MIN: RANGE; RANGE MAX: RANGE
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE |  | KW | DATE | HR | KW | DATE | HR | MIN | MAX
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | OCT 16 | 14 | 7.551 | 1916-10-01 | 13 | 6.286 | NOV 25 | -6.194 | 6.4861 | Oct-16 | 14 | 6.812 | OCT 17 | 14 |  |  |  | 5.965 | 6.812
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | CASE# | KW | DATE | HR | HR | KW | DATE | HR | KW | DATE | HR | KW | NOV 25 | 14 | 7.215 | 1925-11-01 | 13 | 6.17 | NOV 25 | -5.669 | 5.675 | 1992-11-25 | 14 | 6.146 | OCT 17 | 14 |  |  |  | 5.669 | 6.146
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 600 | 6.194 | 1993-10-17 | 13 | 13 | 5.965 | OCT 16 | 14 | 6.656 | OCT 16 | 13 | 6.827 | JUL 26 | 17 | 4.959 | 1902-07-01 | 10 | 4.297 | JUL 26 | -3.634 | 4.275 | 1992-07-26 | 17 | 5.096 | JUL 26 | 16 |  |  |  | 3.634 | 5.096
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 610 | 5.669 | 1993-11-25 | 13 | 13 | 5.824 | NOV 25 | 14 | 6.064 | JAN 13 | 14 | 6.371 | JUL 26 | 17 | 4.4 | 1902-07-01 | 9 | 3.665 | JUL 26 | -3.072 | 3.6083 | 1992-07-26 | 17 | 3.546 | JUN 30 | 17 |  |  |  | 3.072 | 3.704
| = | = | = | = | = | = | = | = | = | [12 empty] | 620 | 3.634 | 1993-07-26 | 16 | 16 | 4.075 | JUL 26 | 17 | 4.43 | JUL 26 | 17 | 4.593 | OCT 16 | 14 | 7.537 | 1916-10-01 | 13 | 6.25 | NOV 25 | -6.161 | 6.4417 | Oct-16 | 14 | 6.771 | OCT 17 | 14
[22 empty] | 630 | 3.072 | 1993-07-26 | 16 | 16 | 3.704 | JUL 26 | 17 | 3.588 | JUL 26 | 17 | 4.116 | OCT 16 | 14 | 7.458 | 1916-10-01 | 13 | 6.143 | NOV 25 | -6.031 | 6.3778 | Oct-17 | 14 | 6.679 | OCT 17 | 14 |  |  |  | 5.831 | 6.679
[22 empty] | 640 | 6.161 | 1993-10-17 | 13 | 13 | 5.892 | OCT 16 | 14 | 6.576 | OCT 16 | 14 | 6.776 | OCT 17 | 14 | 4.901 | 1917-10-01 | 14 | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15 |  |  |  | 2.888 | 3.5667
[22 empty] | 650 | 6.031 | 1993-10-17 | 13 | 13 | 5.831 | OCT 16 | 14 | 6.516 | OCT 16 | 14 | 6.671 | OCT 17 | 15 | 3.973 | 1917-10-01 | 15 | 2.786 | OCT 17 | -1.896 | 2.7917 | Oct-17 | 15 | 3.147 | OCT 17 | 15 |  |  |  | 1.896 | 3.147
[22 empty] | 900 | 2.888 | 1993-10-17 | 14 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | JUL 26 | 17 | 3.777 | 1926-07-01 | 17 | 3.071 | JUL 26 | -2.385 | 3.05 | 1992-07-26 | 17 | 3.505 | JUL 26 | 17 |  |  |  | 2.385 | 3.505
[22 empty] | 910 | 1.896 | 1993-10-17 | 15 | 15 | 2.5 | OCT 21 | 15 | 2.336 | OCT 17 | 15 | 3.277 | JUL 26 | 17 | 3.203 | 1926-07-01 | 17 | 2.486 | JUL 26 | -1.873 | 2.4983 | 1992-07-26 | 17 | 2.304 | JUN 30 | 17 |  |  |  | 1.873 | 2.546
[22 empty] | 920 | 2.385 | 1993-07-26 | 16 | 16 | 2.933 | JUL 26 | 17 | 3.109 | JUL 26 | 17 | 3.487 | OCT 17 | 14 | 4.901 | 1917-10-01 | 14 | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15
[22 empty] | 930 | 1.873 | 1993-07-26 | 17 | 17 | 2.546 | JUL 26 | 17 | 2.388 | JUL 26 | 18 | 3.08 | SEP 02 | 14 | 3.848 | 1902-09-01 | 15 | 2.677 | SEP 02 | -2.033 | 2.6861 | Sep-02 | 15 | 2.867 | SEP 02 | 14 |  |  |  | 2.033 | 2.867
| HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MAY 4 | [20 empty] | 940 | 2.888 | 1993-10-17 | 14 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | JUL 26 | 16 | 1.306 | 1926-07-01 | 16 | 1.179 | JUL 26 | 16 | 1.378 | 1992-07-26 | 16 | 1.403 | JUL 26 | 16 |  |  |  | 0.953 | 1.403
| CASE 600 OR 900 | [20 empty] | 950 | 2.033 | 1993-09-02 | 14 | 14 | 2.621 | SEP 02 | 15 | 2.664 | SEP 2 | 15 | 3.17 | USA DATE: SEP 02; USA HR: 14; USA KW: 3.525; UK-BRE DATE: 1917-10-01; UK-BRE HR: 14; UK-BRE KW: 1.859; SPAIN DATE: NOV 25; SPAIN HR: 14; BEL/UK KW: 2.779; FINLAND DATE: SEP 02; FINLAND HR: 14
| WEST SURFACE | [20 empty] | 960 | 0.953 | 1993-08-16 | 16 | 16 | 1.144 | JUL 26 | 16 | 1.057 | JUL 26 | 16 | 1.37 | JUL 26 | 16 | 0.806 | 1926-07-01 | 16 | 0.799 | JUL 26 | -0.651 | 0.79139 | 1992-07-26 | 16 | 0.79 | JUL 26 | 16
| (USE COLUMN B ONLY) | [20 empty] | 990 | 2.422 | 1993-10-17 | 14 | 14 | 2.912 | SEP 02 | 14 | 3.436 | OCT 17 | 13 | 2.819 |  |  | 1.111 | 1926-07-01 | 15 | 1.105 | JUL 26 | -0.863 | 1.1006 | 1992-07-26 | 16 | 1.126 | JUL 26 | 15
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 195 | 0.651 | 1993-07-26 | 15 | 15 | 0.728 | JUL 26 | 16 | 0.616 | JUL 27 | 15 | 0.853 |  |  | 1.101 | 1926-07-01 | 15 | 1.097 | JUL 26 | -0.476 | 1.0678 | 1992-07-26 | 16 | 1.142 | JUL 26 | 15
0 | COUNTRY: | [20 empty] | 200 | 0.863 | 1993-08-16 | 14 | 14 | 1.017 | JUL 26 | 15 | [6 empty] | 1.347 | 1926-07-01 | 15 | 1.216 | JUL 26 | -1.007 | 1.1836 | 1992-07-26 | 16 | 1.192 | JUL 26 | 15
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 210 | 0.476 | 1993-08-16 | 16 | 16 | 1.017 | JUL 26 | 15 |  |  |  |  | JUL 26 | 15 | 1.342 | 1926-07-01 | 15 | 1.215 | JUL 26 | -0.56 | 1.1789 | 1992-07-26 | 16 | 1.213 | JUL 26 | 15
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 215 | 1.007 | 1993-08-11 | 14 | 14 | 1.166 | JUL 26 | 15 |  |  |  |  | JUL 26 | 15 | 1.878 | 1926-07-01 | 15 | 1.7 | JUL 26 | -1.059 | 1.7078 | 1992-07-26 | 16 | 1.749 | JUL 26 | 15
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 220 | 0.56 | 1993-07-27 | 15 | 15 | 1.166 | JUL 26 | 15 | 0.937 | JUL 27 | 14 | 1.34 | JUL 26 | 15 | 1.542 | 1926-07-01 | 15 | 1.398 | JUL 26 | -0.739 | 1.3614 | 1992-07-26 | 16 | 1.397 | JUL 26 | 15
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 230 | 1.059 | 1993-07-27 | 15 | 15 | 1.646 | JUL 26 | 15 | 1.455 | JUL 27 | 14 | 1.875 | AUG 26 | 14 | 2.582 | 1911-08-01 | 12 | 2.258 | AUG 26 | -3.36 | 3.2278 | Sep-05 | 13 | 4.912 | SEP 05 | 12
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 240 | 0.739 | 1993-07-27 | 15 | 15 | 1.347 | JUL 26 | 15 | 1.119 | JUL 27 | 14 | 1.54 | OCT 16 | 14 | 7.967 | 1925-11-01 | 13 | 6.819 | NOV 25 | -6.356 | 6.7639 | Oct-17 | 14 | 6.867 | OCT 16 | 14
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 250 | 3.36 | 1993-09-05 | 12 | 12 | 3.036 | SEP 05 | 12 | 2.605 | SEP 5 | 11 | 2.59 | OCT 16 | 14 | 5.759 | 1916-10-01 | 13 | 4.63 | NOV 25 | -4.444 | 4.7861 | Oct-16 | 14 | 5.236 | OCT 16 | 14
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 270 | 6.356 | 1993-11-25 | 13 | 13 | 6.641 | NOV 25 | 14 |  |  |  | 7.163 | NOV 25 | 14 | 7.793 | 1923-12-01 | 13 | 6.7 | NOV 25 | -6.269 | 6.2028 | 1992-11-25 | 14 | 6.621 | NOV 25 | 14
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 280 | 4.444 | 1993-10-17 | 13 | 13 | 4.631 | NOV 25 | 13 |  |  |  | 5.22 | JUL 26 | 17 | 5.072 | 1902-07-01 | 10 | 4.336 | JUL 26 | -3.404 | 4.2778 | 1992-07-26 | 17 | 4.929 | JUL 26 | 17
235 | 6 | 9.31 | 9.0004 | 9 | 10.9831 | 9.22 | 7.7154 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.74 |  |  |  | 290 | 6.269 | 1993-01-13 | 13 | 13 | 6.555 | NOV 25 | 14 |  |  |  | 6.91 | JUL 26 | 17 | 4.666 | 1902-07-01 | 9 | 3.669 | JUL 26 | -2.848 | 3.5889 | 1992-07-26 | 17 | 3.425 | JUN 30 | 17
236 | 7 | 36.36 | 36.0015 | 36 | 33.8229 | 31.59 | 31.2881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 31.29 |  |  |  | 300 | 3.404 | 1993-07-26 | 16 | 16 | 4.093 | JUL 26 | 17 |  |  |  | 4.642 | OCT 16 | 14 | 7.332 | 1925-11-01 | 13 | 6.183 | NOV 25 | -5.701 | 6.1778 | Oct-17 | 14 | 6.141 | OCT 16 | 14
237 | 8 | 66.07 | 66.6028 | 66.6 | 59.7762 | 56.9 | 57.9409 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 57.21 |  |  |  | 310 | 2.848 | 1993-07-26 | 16 | 16 | 3.749 | JUN 30 | 17 |  |  |  | 4.186 | JUL 26 | 17 | 0.421 | 1926-07-01 | 16 | 0.356 | JUL 26 | 18 | 0.3625 | 1992-07-26 | 18 | 0.345 | JUL 26 | 18
238 | 9 | 92.71 | 94.8038 | 94.8 | 83.0745 | 80.12 | 81.9063 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 80.81 |  |  |  | 320 | 5.701 | 1993-11-25 | 13 | 13 | 5.946 | NOV 25 | 14 |  |  |  | 6.484 | JUL 26 | 16 | 0.712 | 1926-07-01 | 15 | 0.612 | JUL 26 | 17 | 0.61333 | 1992-07-26 | 17 | 0.572 | JUL 26 | 17
239 | 10 | 113.11 | 117.0048 | 117 | 104.629 | 100.9 | 100.6192 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 99.24 |  |  |  | 395 | 0 |  |  |  | 0.362 | JUL 26 | 18 | 0 |  |  | 0.394 | JUL 26 | 15 | 0.863 | 1926-07-01 | 15 | 0.724 | JUL 26 | -0.035 | 0.74306 | 1992-07-26 | 17 | 0.71 | JUL 26 | 17
240 | 11 | 148.79 | 157.8065 | 157.8 | 132.0397 | 128.06 | 133.4601 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 131.23 |  |  |  | 400 | 0 |  |  |  | 0.581 | JUL 26 | 17 | 0.265 | JUL 27 | 17 | 0.666 | JUL 26 | 15 | 1.078 | 1926-07-01 | 15 | 0.938 | JUL 26 | -0.258 | 0.93778 | 1992-07-26 | 16 | 0.921 | JUL 26 | 15
241 | 12 | 158.81 | 166.8069 | 166.8 | 140.236 | 137.41 | 140.7836 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 138.42 |  |  |  | 410 | 0.035 | 1993-07-27 | 16 | 16 | 0.699 | JUL 26 | 17 | 0.413 | JUL 27 | 17 | 0.814 | JUL 26 | 15 | 1.779 | 1911-08-01 | 13 | 1.575 | JUL 26 | -1.493 | 1.7983 | 1992-09-05 | 13 | 2.578 | SEP 05 | 12
242 | 13 | 159.18 | 166.2068 | 166.2 | 142.6342 | 141.06 | 143.6691 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.31 |  |  |  | 420 | 0.258 | 1993-07-27 | 15 | 15 | 0.923 | JUL 26 | 15 | 0.631 | JUL 27 | 15 | 1.047 | OCT 16 | 14 | 5.615 | 1916-10-01 | 13 | 4.465 | OCT 16 | -4.546 | 4.6861 | Oct-16 | 14 | 5.278 | OCT 17 | 14
243 | 14 | 154.61 | 155.4066 | 155.4 | 137.7338 | 138.78 | 139.5313 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 139.98
244 | 15 | 140.01 | 136.2054 | 136.2 | 123.3077 | 126.87 | 126.0353 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 128.19 |  |  |  | 430 | 1.493 | 1993-08-16 | 14 | 14 | 1.772 | AUG 26 | 14 | 1.427 | AUG 16 | 14 | 1.762 | JUL 27 | 14 | 1.382 | 1927-07-01 | 14 | 1.028 | JUL 27 | -0.585 | 0.98278 | Aug-16 | 14 | 1.358 | SEP 05 | 12
245 | 16 | 114.38 | 108.6046 | 108.6 | 96.8707 | 103.03 | 102.5145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 106.06 |  |  |  | 440 | 4.546 | 1993-10-17 | 13 | 13 | 4.424 | OCT 16 | 14 |  |  |  | 5.053 | SEP 02 | 14 | 3.624 | 1902-09-01 | 14 | 2.432 | SEP 02 | -1.852 | 2.3436 | Sep-02 | 14 | 2.862 | SEP 02 | 14
246 | 17 | 63.55 | 62.4026 | 62.4 | 54.9349 | 61.13 | 56.0031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 59 |  |  |  | 800 | 0.585 | 1993-07-27 | 14 | 14 | 0.967 | AUG 16 | 14 | 0.743 | JUL 28 | 14 | 1.352
247 | 18 | 32.2 | 31.8013 | 31.8 | 26.165 | 28.89 | 27.594 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27.75 |  |  |  | 810 | 1.852 | 1993-09-02 | 14 | 14 | 2.357 | AUG 26 | 14 |  |  |  | 2.991
248 | 19 | 6.81 | 6.6003 | 6.6 | 5.4293 | 7.34 | 5.6434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.66 |  |  |  | FREE-FLOAT TEMPERATURE OUTPUT | [11 empty] | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | OCT 16 | 15 | 69.81 | 1916-10-01 | 16 | 64.9 | OCT 16 | 16 | 65.25 | Oct-17 | 16 | 65.25 | OCT 15 | 16
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | CASE# | TMP (C) | DATE | HR | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | SEP 02 | 15 | 43.44 | 1902-09-01 | 16 | 43 | SEP 02 | 15 | 42.46 | Oct-17 | 15 | 43.17 | SEP 15 | 15
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 600FF | 64.929 | 1993-10-17 | 15 | 15 | 65.11 | OCT 16 | 15 | 69.5 | OCT 17 | 15 | 68.6 | OCT 16 | 15 | 68.49 | 1916-10-01 | 16 | 63.3 | OCT 16 | 16 | 63.74 | Oct-17 | 16 | 63.82 | OCT 16 | 16
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 900FF | 41.812 | 1993-10-17 | 15 | 15 | 43.44 | SEP 02 | 16 | 42.7 | SEP 02 | 15 | 44.8 | SEP 02 | 15 | 35.65 | 1902-09-01 | 16 | 36.1 | SEP 02 | 16 | 35.67 | Sep-02 | 15 | 37.58 | SEP 15 | 16
[22 empty] | 650FF | 63.236 | 1993-10-17 | 15 | 15 | 63.45 | OCT 16 | 15 | 68.2 | OCT 17 | 15 | 67 | OCT 17 | 15 | 51.21 | 1917-10-01 | 16 | 50.2 | OCT 17 | 15 | 55.34 | Oct-17 | 15 | 48.92 | OCT 15 | 15
[22 empty] | 950FF | 35.54 | 1993-09-02 | 16 | 16 | 36.23 | SEP 02 | 16 | 35.9 | SEP 02 | 16 | 38.5
[22 empty] | 960 | 48.943 | 1993-10-17 | 15 | 15 | 48.88 | OCT 06 | 15 | 49 | OCT 17 | 15 | 51 | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
[22 empty] | MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA
[22 empty] | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR
[22 empty] | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | JAN 04 | 7 | -9.96 | 1920-01-01 | 24 | -17.8 | JAN 04 | 8 | -17.81 | Jan-04 | 7 | -18.47 | JAN 08 | 9
[22 empty] | CASE# | TMP (C) | DATE | HR | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | JAN 04 | 8 | -3.94 | 1904-01-01 | 8 | -4 | JAN 04 | 8 | -6.38 | Jan-04 | 8 | -5.64 | JAN 08 | 9
| HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 14 | [20 empty] | 600FF | -15.565 | 1993-01-04 | 7 | 7 | -17.05 | JAN 04 | 8 | -18.8 | JAN 04 | 8 | -18 | JAN 04 | 2 | -9.97 | 1916-01-01 | 6 | -22.9 | JAN 04 | 2 | -22.83 | Jan-04 | 7 | -22.91 | JAN 02 | 23
| CASE 600 | [20 empty] | 900FF | -1.647 | 1993-01-04 | 8 | 8 | -3.15 | JAN 04 | 8 | -4.3 | JAN 04 | 8 | -4.5 | JAN 04 | 7 | -9.83 | 1908-12-01 | 1 | -20.2 | JAN 04 | 7 | -19.34 | Jan-04 | 7 | -19.96 | JAN 07 | 22
| SOUTH SURFACE | [20 empty] | 650FF | -22.564 | 1993-01-04 | 6 | 6 | -22.96 | JAN 04 | 7 | -21.6 | JAN 04 | 2 | -23 | FEB 06 | 7 | 2.22 | 1906-02-01 | 7 | 1.4 | FEB 06 | 6 | -2.82 | Jan-04 | 8 | -0.39 | FEB 05 | 7
| (USE COLUMN B ONLY) | [20 empty] | 950FF | -19.484 | 1993-01-04 | 6 | 6 | -20.04 | JAN 04 | 7 | -18.6 | JAN 04 | 7 | -19.7
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 960 | 2.729 | 1993-02-06 | 6 | 6 | 1.63 | FEB 06 | 7 | 3.9 | FEB 06 | 7 | 3.1 | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
0 | COUNTRY: | [20 empty] | AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | USA KW: TMP (C); UK-BRE KW: TMP (C); SPAIN KW: TMP (C); BEL/UK KW: TMP (C); FINLAND KW: TMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | USA KW: 25.93; UK-BRE KW: 25.2; SPAIN KW: 24.49; BEL/UK KW: 24.22
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | CASE# | TMP (C) |  |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) | USA KW: 25.72; UK-BRE KW: 25.2; SPAIN KW: 24.47; BEL/UK KW: 24.45
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 600FF | 25.126 |  |  |  | 25.43 |  |  | 24.6 |  |  | 25.48 | USA KW: 19.62; UK-BRE KW: 18.4; SPAIN KW: 17.99; BEL/UK KW: 18.36
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 900FF | 25.453 |  |  |  | 25.93 |  |  | 24.7 |  |  | 25.49 | USA KW: 14.29; UK-BRE KW: 14; SPAIN KW: 14.53; BEL/UK KW: 14.64
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 650FF | 18.234 |  |  |  | 18.69 |  |  | 19.1 |  |  | 18.96 | USA KW: 28.54; UK-BRE KW: 28; SPAIN KW: 28.96; BEL/UK KW: 26.43
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 950FF | 14.14 |  |  |  | 14.26 |  |  | 14.3 |  |  | 14.97
234 | 5 | 0 | 0.54029 | 0.7 | 2.825 | 1.27 | 1.0886 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.08 |  |  |  | 960 | 27.49 |  |  |  | 27.72 |  |  | 28 |  |  | 28.69
235 | 6 | 25.87 | 15.3297 | 20.5 | 27.0562 | 24.28 | 25.7932 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.21
236 | 7 | 52.6 | 34.4328 | 46 | 55.3885 | 52.29 | 53.3893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 52.67
237 | 8 | 79.83 | 55.5566 | 73.4 | 82.404 | 79.31 | 80.1937 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 79.43 |  |  |  | BASIC AND IN-DEPTH MASS EFFECT DELTA CHART - ANNUAL
238 | 9 | 166.73 | 139.4762 | 164.1 | 179.1211 | 166.72 | 178.5571 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 170.67 |  |  |  | ANNUAL HEATING AND ANNUAL SENSIBLE COOLING [MWH]
239 | 10 | 296.45 | 272.6453 | 294.38 | 305.7869 | 295.8 | 304.6694 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 300.5 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
240 | 11 | 390.91 | 372.0415 | 390.75 | 396.7139 | 390.25 | 398.8477 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 395.15 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
241 | 12 | 441.65 | 427.7583 | 443.74 | 443.5116 | 441.16 | 449.7855 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 446.05 |  |  |  | 800-430 Mass, Heating w/ High Cond. Wall El. | -0.03 | -0.54834 | -0.551 | -0.50457 | -0.5651 | -0.48107 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.4966; SPAIN DATE: #N/A; SPAIN HR: #N/A
242 | 13 | 445.59 | 433.4522 | 448.17 | 442.6572 | 444.52 | 452.8075 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 449.13 |  |  |  | 800-430 Mass, Cooling w/ High Cond. Wall El. | -0.611 | -0.52633 | -0.582 | -0.48209 | -0.5613 | -0.45694 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.4819; SPAIN DATE: #N/A; SPAIN HR: #N/A
243 | 14 | 401.73 | 389.6588 | 403.38 | 394.8902 | 400.86 | 408.8874 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 405.03 |  |  |  | 900-600 Mass, Heating | -2.324 | -2.6139 | -2.456 | -2.6607 | -2.7773 | -2.6895 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.691; SPAIN DATE: #N/A; SPAIN HR: #N/A
244 | 15 | 312.89 | 300.3721 | 314 | 303.1678 | 312.83 | 320.8144 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 316.3 |  |  |  | 900-600 Mass, Cooling | -3.108 | -3.4493 | -3.049 | -3.5383 | -3.6741 | -3.5124 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -3.3292; SPAIN DATE: #N/A; SPAIN HR: #N/A
245 | 16 | 187.67 | 174.1119 | 189.16 | 175.5288 | 187.96 | 197.5898 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 190.37 |  |  |  | 940-640 Mass, Heating w/ Heating Setback | -1.293 | -1.54 | -1.47 | -1.5945 | -1.6397 | -1.4836 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.3618; SPAIN DATE: #N/A; SPAIN HR: #N/A
246 | 17 | 83.9 | 64.3006 | 77.4 | 81.5142 | 85.41 | 83.9625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 83.16 |  |  |  | 950-650 Mass, Cooling w/ Night Vent | -4.043 | -4.0559 | -3.568 | -4.1099 | -4.2891 | -3.9907 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -3.8775; SPAIN DATE: #N/A; SPAIN HR: #N/A
247 | 18 | 57.72 | 39.0057 | 50.1 | 54.8088 | 56.38 | 57.4921 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 56.83
248 | 19 | 30.17 | 18.8437 | 23.9 | 26.2621 | 28.15 | 29.6492 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 29.07
249 | 20 | 0 | 1.841 | 2 | 2.3496 | 3.31 | 3.1157 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.02 |  |  |  | BASIC AND IN-DEPTH MASS EFFECT DELTA CHART - PEAK
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | PEAK HEATING AND SENSIBLE COOLING [MWH]
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 800-430 Mass, Heating w/ High Cond. Wall El. | -0.343 | -0.47625 | -0.496 | -0.3926 | -0.445 | -0.44187 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.437; SPAIN DATE: #N/A; SPAIN HR: #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 800-430 Mass, Cooling w/ High Cond. Wall El. | -0.881 | -0.73794 | -0.683 | -0.88353 | -0.822 | -0.76849 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.661; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 900-600 Mass, Heating | -0.704 | -0.57684 | -0.582 | -0.51694 | -0.595 | -0.58042 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.526; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 900-600 Mass, Cooling | -2.611 | -3.1046 | -2.866 | -3.3111 | -3.297 | -3.1057 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.791; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 940-640 Mass, Heating w/ Heating Setback | -0.751 | -1.1705 | -0.999 | -1.4158 | -0.979 | -0.63372 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.821; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 950-650 Mass, Cooling w/ Night Vent | -3.282 | -3.9262 | -2.991 | -3.7506 | -3.759 | -3.5611 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -3.104; SPAIN DATE: #N/A; SPAIN HR: #N/A
BESTEST IN-DEPTH CASES 195 TO 220 DELTA CHART - ANNUAL
| HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 14 | [20 empty] | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
| CASE 600 | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
| WEST SURFACE | [20 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
| (USE COLUMN B ONLY) | [20 empty] | 200-195 Heating Surface Convection | 0.824 | 0.82337 | 1.069 | 1.0358 | 0.9695 | 1.0489 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.0135; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 200-195 Cooling Surface Convection | 0.127 | 0.19471 | 0.207 | 0.20256 | 0.1894 | 0.19691 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.2046; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 | COUNTRY: | [20 empty] | 210-200 Heating Ext IR (Int IR "off") | 0.586 | 1.1529 | 1.305 | 0.94118 | 1.3967 | 1.2866 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.2017; SPAIN DATE: #N/A; SPAIN HR: #N/A
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 210-200 Cooling Ext IR (Int IR "off") | -0.151 | -0.29717 | -0.339 | -0.25418 | -0.2819 | -0.32926 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.3336; SPAIN DATE: #N/A; SPAIN HR: #N/A
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 220-215 Heating Ext IR (Int IR "on") | 0.725 | 1.3597 | 1.481 | 1.0497 | 1.5446 | 1.4244 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.3945; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 220-215 Cooling Ext IR (Int IR "on") | -0.149 | -0.33519 | -0.372 | -0.26756 | -0.3186 | -0.35281 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.3632; SPAIN DATE: #N/A; SPAIN HR: #N/A
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 215-200 Heating Int IR (Ext IR "off") | 0.611 | 0.49316 | 0.471 | 0.30004 | 0.2607 | 0.30051 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.4695; SPAIN DATE: #N/A; SPAIN HR: #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 220-210 Heating Int IR (Ext IR "on") | 0.75 | 0.70003 | 0.647 | 0.40857 | 0.4086 | 0.43834 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.6623; SPAIN DATE: #N/A; SPAIN HR: #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0.54029 | 0.7 | 2.825 | 1.27 | 1.0886 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.08 |  |  |  | BESTEST IN-DEPTH CASES 195 TO 220 DELTA CHART - PEAK
235 | 6 | 25.87 | 15.3297 | 20.5 | 27.0562 | 24.28 | 25.7932 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.21 |  |  |  | PEAK HEATING AND SENSIBLE COOLING [MWH]
236 | 7 | 52.6 | 34.4328 | 46 | 55.3885 | 52.29 | 53.3893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 52.67 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
237 | 8 | 79.83 | 55.5479 | 73.4 | 81.9746 | 78.93 | 80.1937 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 79.43 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
238 | 9 | 101.35 | 75.5077 | 98.8 | 104.1185 | 101.39 | 102.9649 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 101.86 |  |  |  | 200-195 Heating Surface Convection | 0.47 | 0.43534 | 0.509 | 0.54692 | 0.473 | 0.5568 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.452; SPAIN DATE: #N/A; SPAIN HR: #N/A
239 | 10 | 117.44 | 91.9039 | 119.2 | 119.4839 | 117.25 | 118.7803 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 117.63 |  |  |  | 200-195 Cooling Surface Convection | 0.153 | 0.22092 | 0.266 | 0.26648 | 0.254 | 0.26541 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.245; SPAIN DATE: #N/A; SPAIN HR: #N/A
240 | 11 | 126.74 | 103.7499 | 133.6 | 128.2458 | 126.5 | 127.9971 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 126.77 |  |  |  | 210-200 Cooling Ext IR (Int IR "off") | -0.078 | -0.26955 | -0.302 | -0.22309 | -0.321 | -0.37477 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.313; SPAIN DATE: #N/A; SPAIN HR: #N/A
241 | 12 | 130.36 | 110.2849 | 141.3 | 131.5461 | 130.19 | 131.6306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 130.34 |  |  |  | 220-215 Cooling Ext IR (Int IR on) | -0.057 | -0.26079 | -0.346 | -0.2159 | -0.354 | -0.38409 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.327; SPAIN DATE: #N/A; SPAIN HR: #N/A
242 | 13 | 238.98 | 207.6793 | 238.46 | 258.9316 | 238.72 | 238.8366 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 238.63 |  |  |  | 215-200 Heating Int IR (Ext IR "off") | 0.249 | 0.19396 | 0.212 | 0.13649 | 0.115 | 0.13665 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.222; SPAIN DATE: #N/A; SPAIN HR: #N/A
243 | 14 | 475.13 | 443.3988 | 460.58 | 491.6517 | 471.42 | 475.03 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 475.15 |  |  |  | 215-200 Cooling Int IR (Ext IR "off") | 0.122 | 0.15407 | 0.147 | 0.092921 | 0.168 | 0.093176 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.123; SPAIN DATE: #N/A; SPAIN HR: #N/A
244 | 15 | 672.39 | 644.8859 | 644.63 | 683.8576 | 668.03 | 673.0005 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 673.23 |  |  |  | 220-210 Heating Int IR (Ext IR "on") | 0.257 | 0.2104 | 0.258 | 0.12747 | 0.117 | 0.12878 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.23; SPAIN DATE: #N/A; SPAIN HR: #N/A
245 | 16 | 809.04 | 787.9666 | 771.27 | 811.9781 | 802.57 | 809.0801 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 809.49 |  |  |  | 220-210 Cooling Int IR (Ext IR "on") | 0.143 | 0.16283 | 0.103 | 0.1001 | 0.135 | 0.083849 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.109; SPAIN DATE: #N/A; SPAIN HR: #N/A
246 | 17 | 861.62 | 850.1509 | 818.34 | 853.4406 | 852.47 | 861.5066 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 861.93
247 | 18 | 806.87 | 805.1397 | 758.2 | 778.077 | 789.03 | 806.2411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 806.56
248 | 19 | 578.91 | 590.3427 | 525.64 | 527.4004 | 555.16 | 588.0142 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 588.02 |  |  |  | BESTEST IN-DEPTH CASES 220 TO 270 DELTA CHART - ANNUAL
249 | 20 | 0 | 78.5987 | 19.69 | 70.2141 | 94.52 | 83.7153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 83.7 |  |  |  | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 230-220 Heating Infiltration | 3.474 | 3.146 | 3.239 | 3.4747 | 3.2128 | 3.3665 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 3.3937; SPAIN DATE: #N/A; SPAIN HR: #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  |  |  | 230-220 Cooling Infiltration | 0.381 | 0.38074 | 0.379 | 0.38131 | 0.3788 | 0.39898 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.4054; SPAIN DATE: #N/A; SPAIN HR: #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 240-220 Heating Internal Gains | -1.261 | -1.2237 | -1.234 | -1.1758 | -1.1864 | -1.2106 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.2224; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 240-220 Cooling Internal Gains | 0.484 | 0.37177 | 0.326 | 0.36884 | 0.3456 | 0.33612 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.3324; SPAIN DATE: #N/A; SPAIN HR: #N/A
| Note: Hourly incident solar on horizontal surface is further down (after the hourly heating and cooling load data tables). | [20 empty] | 250-220 Heating Ext Solar Absorptance | -1.644 | -1.6225 | -1.805 | -1.556 | -1.7907 | -1.7631 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.7274; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 250-220 Cooling Ext Solar Abs. | 2.809 | 2.8184 | 2.921 | 2.5717 | 2.8906 | 2.4062 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 2.4789; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 270-220 Heating South Windows | #N/A | -2.3199 | -2.905 | -2.0698 | -2.1493 | -2.2367 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.3737; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 270-220 Cooling South Windows | #N/A | 6.6602 | 6.148 | 6.9116 | 6.7324 | 6.7908 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 6.7575; SPAIN DATE: #N/A; SPAIN HR: #N/A
| HOURLY FREE FLOAT TEMPERATURE DATA | [20 empty] | BESTEST IN-DEPTH CASES 220 TO 270 DELTA CHART - PEAK
| CASE 600FF FEB 1 | [20 empty] | PEAK HEATING AND SENSIBLE COOLING [MWH]
| (USE COLUMN B ONLY) | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
0 | COUNTRY: | [20 empty] | 230-220 Heating Infiltration | 1.588 | 1.2935 | 1.36 | 1.6241 | 1.372 | 1.4367 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.473; SPAIN DATE: #N/A; SPAIN HR: #N/A
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | 230-220 Cooling Infiltration | 0.658 | 0.61968 | 0.694 | 0.6564 | 0.689 | 0.72555 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.714; SPAIN DATE: #N/A; SPAIN HR: #N/A
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 240-220 Heating Internal Gains | -0.2 | -0.18795 | -0.178 | -0.18492 | -0.183 | -0.18548 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.178; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 240-220 Cooling Internal Gains | 0.198 | 0.18623 | 0.178 | 0.18145 | 0.18 | 0.18157 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.177; SPAIN DATE: #N/A; SPAIN HR: #N/A
294 | 1 | 13 | 7.3199 | 4.4672 | 5.443 | 6 | 4.8678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.1 |  |  |  | 250-220 Cooling Ext Solar Absorpance | 1.577 | 1.6815 | 1.711 | 1.6821 | 2.022 | 1.72 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.717; SPAIN DATE: #N/A; SPAIN HR: #N/A
295 | 2 | 10.3 | 5.475 | 2.8568 | 3.8072 | 4.1 | 3.1842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.6 |  |  |  | 270-220 Cooling South Windows | #N/A | 5.9025 | 4.792 | 5.6543 | 5.601 | 5.6695 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 5.022; SPAIN DATE: #N/A; SPAIN HR: #N/A
296 | 3 | 7.9 | 3.8429 | 1.4091 | 2.3742 | 2.48 | 1.7232 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2
297 | 4 | 5.7 | 2.3514 | -0.016476 | 1.0857 | 0.99 | 0.38989 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.1
298 | 5 | 3.8 | 1.0503 | -1.2245 | -0.0051534 | -0.3 | -0.73229 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.04 |  |  |  | BESTEST IN-DEPTH CASES 270 TO 320 DELTA CHART - ANNUAL
299 | 6 | 2.1 | -0.033328 | -2.2862 | -0.89643 | -1.35 | -1.6653 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.03 |  |  |  | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
300 | 7 | 0.7 | -1.0231 | -3.193 | -1.7104 | -2.34 | -2.5318 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.82 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
301 | 8 | 0.1 | -0.98405 | -3.3337 | -1.4759 | -2.4 | -1.339 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.13 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
302 | 9 | 1.7 | 2.4994 | -0.19628 | 2.7076 | 1.57 | 4.1068 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.82 |  |  |  | 280-270 Cooling Cavity Albedo | #N/A | -2.2745 | -2.483 | -2.3386 | -2.1028 | -2.4804 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.2697; SPAIN DATE: #N/A; SPAIN HR: #N/A
303 | 10 | 6.1 | 9.5334 | 6.8013 | 9.9288 | 9.22 | 11.9724 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 12.84 |  |  |  | 320-270 Heating Thermostat | #N/A | -0.66901 | -0.674 | -0.61416 | -0.6065 | -0.60003 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.6546; SPAIN DATE: #N/A; SPAIN HR: #N/A
304 | 11 | 12.5 | 17.965 | 15.6352 | 18.7293 | 18.48 | 20.6983 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.68 |  |  |  | 320-270 Cooling Thermostat | #N/A | -2.4123 | -2.278 | -2.5356 | -2.3955 | -2.5008 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.4577; SPAIN DATE: #N/A; SPAIN HR: #N/A
305 | 12 | 20.2 | 26.9295 | 25.0661 | 28.01 | 28.14 | 29.8333 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30.88 |  |  |  | 290-270 Cooling South Shading | #N/A | -1.6611 | -1.388 | -1.779 | -1.988 | -1.8273 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.6116; SPAIN DATE: #N/A; SPAIN HR: #N/A
306 | 13 | 28.5 | 35.5894 | 34.0622 | 36.5705 | 37.38 | 38.2109 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 39.35 |  |  |  | 300-270 Cooling E&W Windows | #N/A | -2.2158 | -1.893 | -2.3695 | -2.2705 | -2.3755 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.2304; SPAIN DATE: #N/A; SPAIN HR: #N/A
307 | 14 | 36.1 | 42.8259 | 41.1697 | 43.3942 | 44.87 | 44.2314 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44.4 |  |  |  | 310-300 Heating E&W Shading | #N/A | 0.26199 | 0.386 | 0.26662 | 0.5717 | 0.43695 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.4126; SPAIN DATE: #N/A; SPAIN HR: #N/A
308 | 15 | 41.9 | 47.0783 | 46.07 | 46.9798 | 48.81 | 47.0105 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 47.25 |  |  |  | 310-300 Cooling E&W Shading | #N/A | -1.3032 | -1.403 | -1.4825 | -1.9102 | -1.5887 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.5437; SPAIN DATE: #N/A; SPAIN HR: #N/A
309 | 16 | 45.4 | 48.2109 | 48.1263 | 47.5927 | 49.81 | 46.9306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 47.1
310 | 17 | 46.3 | 45.9023 | 46.582 | 44.8818 | 47.28 | 43.4741 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 43.75
311 | 18 | 44 | 39.9832 | 41.232 | 38.7015 | 40.93 | 36.5383 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.64
312 | 19 | 39.5 | 33.3 | 34.5581 | 32.1639 | 33.48 | 29.6668 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30.13 |  |  |  | BESTEST IN-DEPTH CASES 395 TO 600 DELTA CHART - ANNUAL
313 | 20 | 34.4 | 27.5274 | 28.7453 | 26.2951 | 27.37 | 24.2082 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.55 |  |  |  | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
314 | 21 | 29.3 | 22.5321 | 23.5942 | 21.5268 | 22.09 | 19.2617 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19.67 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
315 | 22 | 24.6 | 18.1055 | 18.976 | 17.0314 | 17.43 | 15.0331 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.29 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
316 | 23 | 20.2 | 14.1487 | 14.9392 | 13.2781 | 13.28 | 11.2196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.61 |  |  |  | 400-395 Low Mass, Heating Surf. Conv. & IR | 1.341 | 1.6808 | 1.902 | 1.7066 | 1.7443 | 1.8611 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.8521; SPAIN DATE: #N/A; SPAIN HR: #N/A
317 | 24 | 16.3 | 10.8188 | 11.505 | 10.2079 | 9.82 | 8.1223 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 8.59 |  |  |  | 410-400 Low Mass, Heating Infiltration | 1.724 | 1.5093 | 1.614 | 1.7325 | 1.6022 | 1.6757 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.6881; SPAIN DATE: #N/A; SPAIN HR: #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 420-410 Low Mass, Heating Int. Gains | -1.231 | -1.2106 | -1.228 | -1.1745 | -1.1852 | -1.2086 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.2169; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 430-420 Low Mass, Heating Ext. Solar Abs. | -1.228 | -1.3804 | -1.479 | -1.2857 | -1.4821 | -1.3858 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.4093; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 430-420 Low Mass, Cooling Ext Solar Abs. | 0.856 | 0.76554 | 0.825 | 0.70305 | 0.8108 | 0.62959 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.6331; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 600-430 Low Mass, Heating S. Window | -1.121 | -1.4613 | -1.907 | -1.2958 | -1.1829 | -1.347 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.4692; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 600-430 Low Mass, Cooling S. Window | 4.738 | 5.007 | 4.488 | 5.1714 | 5.2091 | 5.0405 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 5.0397; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 440-600 Low Mass, Heating Cavity Albedo | #N/A | 0.16318 | 0.283 | 0.17569 | 0.1419 | 0.21713 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.2533; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 440-600 Low Mass, Cooling Cavity Albedo | #N/A | -1.9278 | -1.974 | -1.942 | -1.7477 | -2.0384 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.8663; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 810-900 High Mass, Heating Cavity Albedo | #N/A | 0.65862 | 0.863 | 0.67814 | 0.6003 | 0.79572 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.7783; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 810-900 High Mass, Cooling Cavity Albedo | #N/A | -0.98312 | -1.026 | -0.98095 | -0.8821 | -0.97261 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.9952; SPAIN DATE: #N/A; SPAIN HR: #N/A
HOURLY FREE FLOAT TEMPERATURE DATA
| CASE 900FF FEB 1 | [20 empty] | BESTEST IN-DEPTH CASES 395 TO 600 DELTA CHART - ANNUAL
| (USE COLUMN B ONLY) | [20 empty] | PEAK HEATING AND SENSIBLE COOLING [MWH]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
0 | COUNTRY: | [20 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | 400-395 Low Mass, Heating Surf. Conv. & IR | 0.611 | 0.68193 | 0.778 | 0.74028 | 0.698 | 0.71723 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.694; SPAIN DATE: #N/A; SPAIN HR: #N/A
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 400-395 Low Mass, Cooling Surf. Conv. & IR | 0.251 | 0.13615 | 0.149 | 0.22943 | 0.162 | 0.10678 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.163; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 410-400 Low Mass, Heating Infiltration | 0.779 | 0.60131 | 0.68 | 0.81203 | 0.685 | 0.71836 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.736; SPAIN DATE: #N/A; SPAIN HR: #N/A
294 | 1 | 15.4 | 14.7379 | 11.7017 | 12.938 | 13.28 | 12.3543 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 12.23 |  |  |  | 410-400 Low Mass, Cooling Infiltration | 0.213 | 0.20623 | 0.252 | 0.22094 | 0.168 | 0.2317 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.246; SPAIN DATE: #N/A; SPAIN HR: #N/A
295 | 2 | 14.8 | 14.2075 | 11.245 | 12.4251 | 12.7 | 11.8184 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.76 |  |  |  | 420-410 Low Mass, Heating Int. Gains | -0.2 | -0.18445 | -0.178 | -0.18492 | -0.183 | -0.18548 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.178; SPAIN DATE: #N/A; SPAIN HR: #N/A
296 | 3 | 14.2 | 13.7002 | 10.7932 | 11.9298 | 12.17 | 11.3192 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.24 |  |  |  | 420-410 Low Mass, Cooling Int. Gains | 0.197 | 0.20865 | 0.208 | 0.20469 | 0.212 | 0.21039 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.195; SPAIN DATE: #N/A; SPAIN HR: #N/A
297 | 4 | 13.6 | 13.1833 | 10.3008 | 11.432 | 11.64 | 10.8039 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10.73 |  |  |  | 430-420 Low Mass, Cooling Ext. Solar Abs. | 0.959 | 0.93129 | 0.923 | 0.89683 | 1.038 | 0.89001 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.791; SPAIN DATE: #N/A; SPAIN HR: #N/A
298 | 5 | 13 | 12.7111 | 9.9029 | 10.9913 | 11.15 | 10.3478 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10.35 |  |  |  | 600-430 Low Mass, Cooling S. Window | 3.483 | 4.6412 | 3.582 | 4.4222 | 4.319 | 4.3417 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 3.932; SPAIN DATE: #N/A; SPAIN HR: #N/A
299 | 6 | 12.4 | 12.2668 | 9.4738 | 10.5804 | 10.72 | 9.9295 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.88 |  |  |  | 440-600 Low Mass, Cooling Cavity Albedo | #N/A | -1.8155 | -1.656 | -1.6656 | -1.514 | -1.7382 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.425; SPAIN DATE: #N/A; SPAIN HR: #N/A
300 | 7 | 11.8 | 11.8353 | 9.0975 | 10.1741 | 10.25 | 9.4998 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.49 |  |  |  | 810-900 High Mass, Cooling Cavity Albedo | #N/A | -0.96595 | -0.616 | -0.77023 | -0.717 | -0.8272 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.585; SPAIN DATE: #N/A; SPAIN HR: #N/A
301 | 8 | 11.2 | 11.941 | 8.9582 | 10.3241 | 10.14 | 9.799 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.96 |  |  |  | BESTEST Indepth South Window Delta Annual Cooling and Heating
302 | 9 | 11.8 | 13.2165 | 9.8876 | 11.7504 | 11.22 | 11.4018 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.8 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
303 | 10 | 13.4 | 15.2859 | 11.7551 | 13.8083 | 13.19 | 13.4628 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 13.97 |  |  |  | 600-430 Low Mass, Heating S. Window | -1.121 | -1.4613 | -1.907 | -1.2958 | -1.1829 | -1.347 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.4692; SPAIN DATE: #N/A; SPAIN HR: #N/A
304 | 11 | 15.7 | 17.5497 | 13.9547 | 15.9577 | 15.41 | 15.5991 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.24 |  |  |  | 600-430 Low Mass, Cooling S. Window | 4.738 | 5.007 | 4.488 | 5.1714 | 5.2091 | 5.0405 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 5.0397; SPAIN DATE: #N/A; SPAIN HR: #N/A
305 | 12 | 18.4 | 19.8553 | 16.2133 | 18.2069 | 17.71 | 17.9031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.63 |  |  |  | 900-800 High Mass, Heating S. Window | -3.415 | -3.5268 | -3.812 | -3.4519 | -3.3951 | -3.5554 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -3.6636; SPAIN DATE: #N/A; SPAIN HR: #N/A
306 | 13 | 21.3 | 22.0025 | 18.3357 | 20.4419 | 20.03 | 20.0527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20.81 |  |  |  | 900-800 High Mass, Cooling S. Window | 2.241 | 2.084 | 2.021 | 2.1152 | 2.0963 | 1.985 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 2.1924; SPAIN DATE: #N/A; SPAIN HR: #N/A
307 | 14 | 23.2 | 23.2661 | 19.6982 | 22.0116 | 21.78 | 21.5258 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.7
308 | 15 | 24.8 | 23.5646 | 20.6912 | 22.7239 | 22.59 | 22.2103 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.36
309 | 16 | 25.4 | 23.5055 | 21.0435 | 22.8195 | 22.89 | 22.2681 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.31
310 | 17 | 24.6 | 22.7021 | 20.5729 | 22.102 | 22.44 | 21.5145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.49 |  |  |  | BESTEST BASIC Window Types (Delta) Annual Heating and Cooling
311 | 18 | 23.5 | 20.9392 | 19.2453 | 20.4887 | 21.07 | 19.867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19.62 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
312 | 19 | 22.6 | 19.7278 | 18.0354 | 19.2192 | 19.67 | 18.5155 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.41 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
313 | 20 | 21.9 | 18.9536 | 17.2201 | 18.324 | 18.77 | 17.6825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.52 |  |  |  | 660-600 Low-E Windows, Heating | -0.476 | -0.3908 | -0.226 | -0.61764 | -0.575 | -0.71389 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.5082
314 | 21 | 20.8 | 18.2399 | 16.476 | 17.5351 | 17.93 | 16.825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.71 |  |  |  | 660-600 Low-E Windows, Cooling | -2.808 | -2.5734 | -2.172 | -2.7955 | -2.9432 | -2.8133 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.6578
315 | 22 | 20 | 17.5304 | 15.7483 | 16.7569 | 17.11 | 16.0591 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.88 |  |  |  | 670-600 Single-Pane Windows, Heating | 1.434 | 1.3074 | 1.526 | 1.2918 | 1.613 | 1.6363 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.4612
316 | 23 | 19.2 | 16.8299 | 15.107 | 15.9944 | 16.31 | 15.2703 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.19 |  |  |  | 670-600 Single-Pane Windows, Cooling | 0.717 | 0.66462 | 0.522 | 0.59566 | 0.3585 | 0.41828 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.217
317 | 24 | 18.1 | 16.228 | 14.5494 | 15.3612 | 15.65 | 14.6249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 14.61
| = | = | = | = | = | = | = | = | = | [8 empty] | =
BESTEST BASIC Window Types (Delta) Peak Heating and Cooling
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | 660-600 Low-E Windows, Heating | -0.635 | -0.26192 | -0.237 | -0.3733 | -0.382 | -0.40371 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.335
[22 empty] | 660-600 Low-E Windows, Cooling | -2.307 | -2.548 | -2.067 | -2.5812 | -2.663 | -2.5883 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.174
[22 empty] | 670-600 Single-Pane Windows, Heating | 0.867 | 0.63519 | 0.777 | 0.6491 | 0.764 | 0.86207 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.68
[22 empty] | 670-600 Single-Pane Windows, Cooling | 0.567 | 0.44432 | 0.417 | 0.45463 | 0.289 | 0.35556 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.332
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FFV JULY 14
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | BESTEST BASIC Insulation (Delta) Annual Heating and Cooling
0 | COUNTRY: | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 680-600 600 with Greater Insulation, Heating | -1.831 | -2.2067 | -2.315 | -2.1447 | -2.2299 | -2.2173 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.2355
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 680-600 600 with Greater Insulation, Cooling | 0.116 | 0.51669 | 0.5 | 0.41686 | 0.3676 | 0.53023 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.6054
294 | 1 | 21.7 | 19.8311 | 19.6725 | 19.8711 | 19.86 | 20.0209 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19.53 |  |  |  | 685-600 600 with 20/20 Tstat, Heating | 0.482 | 0.58167 | 0.599 | 0.55275 | 0.5415 | 0.53862 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.5887
295 | 2 | 20.1 | 19.0165 | 18.88 | 19.0627 | 19.01 | 18.7675 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.75 |  |  |  | 685-600 600 with 20/20 Tstat, Cooling | 3.308 | 2.9461 | 2.806 | 3.0918 | 2.9596 | 3.0718 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 3.0107
296 | 3 | 19 | 18.1137 | 17.7669 | 18.14 | 18.1 | 18.213 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.57 |  |  |  | 695-685 685 with Greater Insulation, Heating | -1.823 | -2.1592 | -2.261 | -2.0752 | -2.1714 | -2.1504 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.1481
297 | 4 | 17.8 | 16.994 | 16.6508 | 17.0158 | 16.97 | 16.7605 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.45 |  |  |  | 695-685 685 with Greater Insulation, Cooling | -0.375 | 0.1149 | 0.148 | 0.052759 | 0.0276 | 0.18778 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.301
298 | 5 | 16.6 | 15.8658 | 15.4711 | 15.8836 | 15.83 | 15.8849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.28 |  |  |  | 980-900 900 with Greater Insulation, Heating | -1.006 | -1.1331 | -1.325 | -1.2527 | -1.2336 | -1.3636 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.3597
299 | 6 | 16.6 | 16.1929 | 17.1247 | 16.3875 | 16.09 | 16.0945 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.18 |  |  |  | 980-900 900 with Greater Insulation, Cooling | 0.787 | 1.5314 | 1.375 | 1.2231 | 1.2868 | 1.2514 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.3242
300 | 7 | 18.2 | 18.4147 | 19.397 | 18.7611 | 18.49 | 18.6396 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19.63 |  |  |  | 985-900 900 with 20/20 Tstat, Heating | 1.075 | 0.74132 | 0.688 | 0.70563 | 0.6986 | 0.72238 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.778
301 | 8 | 20.3 | 20.1417 | 20.5125 | 20.8898 | 20.94 | 20.6119 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.35 |  |  |  | 985-900 900 with 20/20 Tstat, Cooling | 4.559 | 3.7698 | 3.497 | 3.8704 | 3.7616 | 3.8463 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 3.8589
302 | 9 | 22.3 | 22.2539 | 22.8099 | 23.2971 | 23.29 | 23.2169 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 23.92 |  |  |  | 995-985 985 with Greater Insulation, Heating | -1.471 | -1.365 | -1.509 | -1.3628 | -1.3785 | -1.4594 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.5237
303 | 10 | 24.9 | 25.3076 | 25.8855 | 26.426 | 26.23 | 26.4995 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27.73 |  |  |  | 995-985 985 with Greater Insulation, Cooling | 0.209 | 0.9685 | 0.891 | 0.84367 | 0.8995 | 0.95032 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.9106
304 | 11 | 28.3 | 29.4735 | 29.838 | 30.6202 | 30.05 | 30.7733 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32.5
305 | 12 | 32.3 | 34.0869 | 34.1747 | 35.2192 | 34.64 | 35.1804 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.74
306 | 13 | 36.2 | 38.0756 | 38.3724 | 39.1876 | 38.99 | 39.0337 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 40.54
307 | 14 | 39.7 | 41.1874 | 41.8987 | 42.1006 | 42.49 | 41.924 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 43.25 |  |  |  | BESTEST BASIC Insulation (Delta) Peak Heating and Cooling
308 | 15 | 42.5 | 43.0949 | 44.2829 | 44.2085 | 44.77 | 43.5674 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44.78 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
309 | 16 | 44.4 | 43.7728 | 45.2962 | 44.886 | 45.78 | 43.8561 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44.69 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
310 | 17 | 45.4 | 43.4747 | 45.2885 | 44.6042 | 45.65 | 43.3487 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 43.97 |  |  |  | 680-600 600 with Greater Insulation, Heating | -1.129 | -1.2426 | -1.224 | -1.152 | -1.206 | -1.2442 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.111
311 | 18 | 41.7 | 42.6822 | 44.6098 | 43.7421 | 44.91 | 42.3948 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 42.77 |  |  |  | 680-600 600 with Greater Insulation, Cooling | 0.111 | 0.57027 | 0.439 | 0.41866 | 0.483 | 0.51086 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.419
312 | 19 | 35.5 | 34.1248 | 33.257 | 34.4834 | 38.29 | 33.6127 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32.62 |  |  |  | 685-600 600 with 20/20 Tstat, Heating | -0.086 | 0.011624 | 0.019 | 0.018741 | 0.019 | 0.015534 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.028
313 | 20 | 31.7 | 30.7295 | 30.0661 | 30.8554 | 31.6 | 29.6146 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 29.26 |  |  |  | 685-600 600 with 20/20 Tstat, Cooling | 0.668 | 0.67846 | 0.649 | 0.7552 | 0.741 | 0.82169 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.679
314 | 21 | 28.6 | 27.846 | 27.4122 | 27.9576 | 28.34 | 27.9251 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 26.82 |  |  |  | 695-685 685 with Greater Insulation, Heating | -1.031 | -1.2365 | -1.199 | -1.1514 | -1.222 | -1.2567 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.133
315 | 22 | 26.5 | 25.8648 | 25.8257 | 25.9916 | 26.14 | 25.3141 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.42 |  |  |  | 695-685 685 with Greater Insulation, Cooling | -0.086 | 0.38129 | 0.284 | 0.22753 | 0.305 | 0.30772 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.33
316 | 23 | 25 | 24.4442 | 24.2308 | 24.5462 | 24.6 | 24.6473 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 23.94 |  |  |  | 980-900 900 with Greater Insulation, Heating | -0.858 | -1.1896 | -1.071 | -1.1497 | -1.16 | -1.1863 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.026
317 | 24 | 23.5 | 22.9121 | 22.4527 | 22.9825 | 22.99 | 22.567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.2 |  |  |  | 980-900 900 with Greater Insulation, Cooling | 0.345 | 0.29156 | 0.374 | 0.40968 | 0.445 | 0.37249 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.339
| = | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 985-900 900 with 20/20 Tstat, Heating | 0.203 | 0.008773 | 0.005 | 0.0079536 | 0.009 | 0.0069624 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.006
[22 empty] | 985-900 900 with 20/20 Tstat, Cooling | 0.938 | 0.84883 | 0.652 | 0.87434 | 0.84 | 0.94464 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.698
[22 empty] | 995-985 985 with Greater Insulation, Heating | -1.043 | -1.0826 | -0.996 | -1.0733 | -1.082 | -1.1235 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.981
[22 empty] | 995-985 985 with Greater Insulation, Cooling | 0.152 | -0.001482 | 0.107 | 0.26266 | 0.218 | 0.2302 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.127
HOURLY FREE FLOAT TEMPERATURE DATA
| CASE 950FFV JULY 14 | [20 empty] | BASIC INSULATION MASS EFFECT DELTA CHART - ANNUAL
| (USE COLUMN B ONLY) | [20 empty] | ANNUAL HEATING AND ANNUAL SENSIBLE COOLING [MWH]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
0 | COUNTRY: | [20 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | 980-680 Mass, Heating with Greater Insulation | -1.499 | -1.5403 | -1.466 | -1.7687 | -1.781 | -1.8358 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.8152
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 980-680 Mass, Cooling with Greater Insulation | -2.437 | -2.4346 | -2.174 | -2.7321 | -2.7549 | -2.7912 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.6104
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 985-685 Mass, Heating with 20/20 Tstat | -1.731 | -2.4542 | -2.367 | -2.5078 | -2.6202 | -2.5058 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.5017
294 | 1 | 23.4 | 21.2148 | 20.9717 | 21.2303 | 21.37 | 21.1154 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20.85 |  |  |  | 985-685 Mass, Cooling with 20/20 Tstat | -1.857 | -2.6256 | -2.358 | -2.7596 | -2.8721 | -2.7378 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.481
295 | 2 | 22.2 | 20.7077 | 20.4879 | 20.7155 | 20.84 | 20.5424 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20.35 |  |  |  | 995-695 Mass, Heating w/ > Insul. & 20/20 Tstat | -1.379 | -1.6601 | -1.615 | -1.7954 | -1.8273 | -1.8147 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.8773
296 | 3 | 21.3 | 20.0478 | 19.6293 | 20.0299 | 20.18 | 19.9172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19.46 |  |  |  | 995-695 Mass, Cooling w/ > Insul. & 20/20 Tstat | -1.273 | -1.772 | -1.615 | -1.9687 | -2.0002 | -1.9753 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.8714
297 | 4 | 20.3 | 19.188 | 18.7479 | 19.1593 | 19.31 | 19.0113 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.57
298 | 5 | 19.3 | 18.2994 | 17.7906 | 18.2535 | 18.4 | 18.1384 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.59
299 | 6 | 19.3 | 18.5567 | 19.3484 | 18.6317 | 18.55 | 18.3188 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19.17
300 | 7 | 20.5 | 20.0938 | 21.0886 | 20.2686 | 20.13 | 19.9757 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21 |  |  |  | BASIC INSULATION MASS EFFECT DELTA CHART - ANNUAL
301 | 8 | 22.1 | 22.4421 | 23.1543 | 22.8727 | 22.07 | 22.5701 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 23.08 |  |  |  | PEAK HEATING AND ANNUAL SENSIBLE COOLING [MWH]
302 | 9 | 23.4 | 23.5009 | 23.8657 | 24.4046 | 24.04 | 24.209 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.06 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
303 | 10 | 24.5 | 24.6745 | 24.7959 | 25.569 | 25.3 | 25.0426 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.36 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
304 | 11 | 25.8 | 26.1394 | 25.9168 | 26.9141 | 26.65 | 26.5298 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 26.83 |  |  |  | 980-680 Mass, Heating with Greater Insulation | -0.433 | -0.52385 | -0.429 | -0.51458 | -0.549 | -0.52258 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.441
305 | 12 | 27.4 | 27.5275 | 27.0556 | 28.1778 | 27.92 | 27.7048 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27.98 |  |  |  | 980-680 Mass, Cooling with Greater Insulation | -2.377 | -3.3833 | -2.931 | -3.3201 | -3.335 | -3.244 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.871
306 | 13 | 28.7 | 28.5007 | 28.1472 | 29.1272 | 28.96 | 28.7071 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 29.02 |  |  |  | 985-685 Mass, Heating with 20/20 Tstat | -0.415 | -0.57969 | -0.596 | -0.52772 | -0.605 | -0.58899 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.548
307 | 14 | 29.8 | 29.1549 | 29.0149 | 29.8598 | 29.78 | 29.4146 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 29.73 |  |  |  | 985-685 Mass, Cooling with 20/20 Tstat | -2.341 | -2.9342 | -2.863 | -3.192 | -3.198 | -2.9827 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.772
308 | 15 | 30.6 | 29.3989 | 29.5372 | 30.2902 | 30.31 | 29.8578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30.09 |  |  |  | 995-695 Mass, Heating w/ > Insul. & 20/20 Tstat | -0.427 | -0.42577 | -0.393 | -0.44966 | -0.465 | -0.45573 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.396
309 | 16 | 31 | 29.2893 | 29.7074 | 30.4309 | 30.52 | 29.9484 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30 |  |  |  | 995-695 Mass, Cooling w/ > Insul. & 20/20 Tstat | -2.103 | -3.3169 | -3.04 | -3.1569 | -3.285 | -3.0602 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.975
310 | 17 | 31.4 | 29.1458 | 29.7175 | 30.4338 | 30.55 | 29.9561 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 29.91
311 | 18 | 31 | 29.0474 | 29.6094 | 30.3524 | 30.53 | 29.8951 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 29.72
312 | 19 | 30.3 | 28.666 | 28.4499 | 29.0273 | 29.51 | 28.9728 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.49
313 | 20 | 29.1 | 27.3534 | 26.9749 | 27.6463 | 27.82 | 27.553 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 26.97
314 | 21 | 28.1 | 26.0894 | 25.7654 | 26.3384 | 26.48 | 26.2179 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.74
315 | 22 | 27 | 25.2973 | 25.2338 | 25.5339 | 25.61 | 25.3225 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.18
316 | 23 | 26 | 24.6727 | 24.4091 | 24.8642 | 24.95 | 24.6889 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.34
317 | 24 | 24.9 | 23.7451 | 23.2527 | 23.8852 | 23.99 | 23.7105 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 23.16
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | BESTEST IN-DEPTH Surface Heat Transfer (Delta) Annual Heating and Cooling
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | 450-600 Const. Int.&Ext. Surf. Coefs., Heating | -0.307 | -0.0023157 | -0.672 | -0.3619 | -0.5117 | -0.63264 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.6509
[22 empty] | 450-600 Const. Int.&Ext. Surf. Coefs., Cooling | 0.35 | -0.22415 | 0.729 | 0.48022 | 0.4514 | 0.75118 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.8835
[22 empty] | 460-600 Const. Interior Surf. Coefs., Heating | -0.222 | 0.062755 | -0.174 | -0.13062 | -0.0995 | -0.21378 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.253
[22 empty] | 460-600 Const. Interior Surf. Coefs., Cooling | 0.438 | 0.026684 | 0.497 | 0.44757 | 0.5673 | 0.46383 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.5682
[22 empty] | 460-450 Auto Exterior Surf. H.T., Heating | 0.085 | 0.065071 | 0.498 | 0.23127 | 0.4122 | 0.41886 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.3979
| HOURLY FREE FLOAT TEMPERATURE DATA | [20 empty] | 460-450 Auto Exterior Surf. H.T., Cooling | 0.088 | 0.25083 | -0.232 | -0.03265 | 0.1159 | -0.28735 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.3153
| CASE 680FF JULY 14 | [20 empty] | 470-600 Const. Exterior Surf. Coefs., Heating | -0.008 | -0.093264 | -0.507 | -0.23051 | -0.4023 | -0.42893 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.4014
| (USE COLUMN B ONLY) | [20 empty] | 470-600 Const. Exterior Surf. Coefs., Cooling | 0.165 | -0.26923 | 0.217 | 0.0023448 | -0.1564 | 0.27637 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.2989
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 470-450 Auto Interior Surf. H.T., Heating | 0.299 | -0.090948 | 0.165 | 0.13138 | 0.1094 | 0.20371 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.2495
0 | COUNTRY: | [20 empty] | 470-450 Auto Interior Surf. H.T., Cooling | -0.185 | -0.045084 | -0.512 | -0.47787 | -0.6078 | -0.47481 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.5846
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
294 | 1 | 27.4 | 19.3025 | 16.0238 | 15.3461 | 16.32 | 14.4417 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 14.56 |  |  |  | BESTEST IN-DEPTH Surface Heat Transfer (Delta) Peak Heating and Cooling
295 | 2 | 24 | 17.2859 | 14.3021 | 13.4846 | 14.25 | 12.548 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 12.77 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
296 | 3 | 20.8 | 15.4125 | 12.6782 | 11.7774 | 12.37 | 10.8267 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.04 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
297 | 4 | 17.8 | 13.6262 | 11.0975 | 10.1946 | 10.6 | 9.1997 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.41 |  |  |  | 450-600 Const. Int.&Ext. Surf. Coefs., Heating | -0.266 | -0.041917 | -0.282 | -0.10461 | -0.186 | -0.32158 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.162
298 | 5 | 15 | 11.9969 | 9.689 | 8.775 | 9.01 | 7.7578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 8.08 |  |  |  | 450-600 Const. Int.&Ext. Surf. Coefs., Cooling | 0.162 | -0.30121 | 0.641 | 0.11476 | 0.308 | 0.26769 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.79
299 | 6 | 12.4 | 10.5252 | 8.334 | 7.5063 | 7.61 | 6.48 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.74 |  |  |  | 460-600 Const. Interior Surf. Coefs., Heating | -0.2 | -0.04888 | -0.055 | -0.11337 | -0.127 | -0.19922 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.082
300 | 7 | 10.1 | 9.1662 | 7.1316 | 6.3475 | 6.29 | 5.2952 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.6 |  |  |  | 460-600 Const. Interior Surf. Coefs., Cooling | 0.154 | -0.23813 | 0.48 | 0.0226 | 0.111 | 0.023202 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.543
301 | 8 | 8.7 | 8.8545 | 6.5882 | 6.2878 | 5.9 | 6.1093 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.7 |  |  |  | 460-450 Auto Exterior Surf. H.T., Heating | 0.066 | -0.006963 | 0.227 | -0.0087666 | 0.059 | 0.12236 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.08
302 | 9 | 9.5 | 11.6688 | 8.9979 | 10.0373 | 9.12 | 11.026 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.89 |  |  |  | 460-450 Auto Exterior Surf. H.T., Cooling | -0.008 | 0.063083 | -0.161 | -0.09216 | -0.197 | -0.24449 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.247
303 | 10 | 13.1 | 17.8327 | 15.0347 | 16.5873 | 15.82 | 18.4242 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19.29 |  |  |  | 470-600 Const. Exterior Surf. Coefs., Heating | -0.137 | -0.019557 | -0.228 | 0.0023118 | -0.059 | -0.1274 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.086
304 | 11 | 19.1 | 25.8327 | 23.1553 | 24.697 | 24.43 | 26.9441 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27.85 |  |  |  | 470-600 Const. Exterior Surf. Coefs., Cooling | 0.045 | -0.093327 | 0.148 | 0.092071 | 0.214 | 0.27425 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.159
305 | 12 | 26.7 | 34.849 | 32.2721 | 33.6544 | 33.78 | 36.1278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 37.1 |  |  |  | 470-450 Auto Interior Surf. H.T., Heating | 0.129 | 0.02236 | 0.054 | 0.10692 | 0.127 | 0.19418 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.076
306 | 13 | 35.2 | 43.9435 | 41.4162 | 42.5122 | 43.16 | 44.8321 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.92 |  |  |  | 470-450 Auto Interior Surf. H.T., Cooling | -0.117 | 0.20788 | -0.493 | -0.022689 | -0.094 | 0.0065584 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.631
307 | 14 | 43.4 | 51.6986 | 49.1534 | 49.7746 | 51.16 | 51.5938 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 51.95
308 | 15 | 50.2 | 57.0436 | 55.1901 | 54.3914 | 56.13 | 55.5469 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 56.06
309 | 16 | 55.1 | 59.5967 | 58.6456 | 56.3144 | 58.45 | 56.7937 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 57.31
310 | 17 | 57.3 | 58.7261 | 58.7506 | 54.9811 | 57.42 | 54.6584 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 55.41 |  |  |  | BESTEST BASIC Shading and Window Orientation (Delta) Annual Heating and Cooling
311 | 18 | 56.3 | 54.2792 | 55.2721 | 50.2114 | 52.78 | 49.111 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 49.91 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
312 | 19 | 53 | 49.0597 | 50.4057 | 44.9265 | 47.02 | 43.4177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44.61 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
313 | 20 | 48.8 | 44.294 | 45.8603 | 39.9705 | 42.06 | 38.6121 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 39.77 |  |  |  | 610-600 Low Mass, S.Shade Heating | 0.113 | 0.073669 | 0.097 | 0.050431 | 0.165 | 0.08851 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.0942
314 | 21 | 44.3 | 39.9085 | 41.5737 | 35.6029 | 37.49 | 34.0685 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 35.56 |  |  |  | 610-600 Low Mass, S.Shade Cooling | -1.523 | -1.5313 | -1.259 | -1.6943 | -1.9293 | -1.6627 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.4831
315 | 22 | 39.8 | 35.8862 | 37.5376 | 31.6493 | 33.3 | 30.1063 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 31.44 |  |  |  | 910-900 High Mass, S. Shade Heating | 0.437 | 0.26879 | 0.269 | 0.29205 | 0.4825 | 0.31776 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.3148
316 | 23 | 35.4 | 32.1123 | 33.8308 | 28.034 | 29.35 | 26.2987 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27.76 |  |  |  | 910-900 High Mass, S. Shade Cooling | -1.23 | -1.049 | -0.893 | -1.1053 | -1.2048 | -1.0763 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.0162
317 | 24 | 31.2 | 28.6933 | 30.4633 | 24.8425 | 25.88 | 22.9692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.5 |  |  |  | 620-600 Low Mass, E&W Or., Heating | 0.32 | 0.10084 | 0.25 | 0.1607 | 0.1523 | 0.21543 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.248
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 620-600 Low Mass, E&W Or., Cooling | -1.418 | -1.8338 | -1.523 | -1.9675 | -1.9161 | -1.9389 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.8457
[22 empty] | 920-900 High Mass, E&W Or., Heating | 1.774 | 1.5772 | 1.668 | 1.6728 | 1.715 | 1.7927 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.7922
[22 empty] | 920-900 HIgh Mass, E&W Or., Cooling | 0.414 | 0.32538 | 0.323 | 0.2421 | 0.3267 | 0.28174 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.2095
[22 empty] | 630-620 Low Mass, E&W Shd., Heating | 0.553 | 0.26235 | 0.38 | 0.29847 | 0.5363 | 0.4196 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.4053
[22 empty] | 630-620 Low Mass, E&W Shd., Cooling | -1.33 | -1.0589 | -1.122 | -1.2235 | -1.6504 | -1.2678 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.2328
[22 empty] | 930-920 High Mass, E&W Shd., Heating | 0.77 | 0.56758 | 0.674 | 0.6573 | 0.9779 | 0.7774 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.7611
[22 empty] | 930-920 High Mass, E&W Shd., Cooling | -0.967 | -0.71422 | -0.798 | -0.81173 | -1.1606 | -0.87711 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.8688
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 980FF JULY 14
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | BESTEST BASIC Shading and Window Orientation (Delta) Peak Heating and Cooling
0 | COUNTRY: | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 610-600 Low Mass, S.Shade Heating | -0.089 | 0.000526 | 0.004 | -0.012584 | 0.005 | 0.00060921 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.004
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 610-600 Low Mass, S.Shade Cooling | -0.184 | -0.048825 | -0.091 | -0.21703 | -0.259 | -0.17795 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.265
294 | 1 | 26.6 | 27.6665 | 24.2654 | 22.7451 | 23.79 | 22.2363 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.81 |  |  |  | 910-900 High Mass, S. Shade Heating | 0.21 | 0.025635 | 0.021 | 0.011437 | 0.051 | 0.020717 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.02
295 | 2 | 25.8 | 27.1526 | 23.841 | 22.2438 | 23.19 | 21.7134 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.34 |  |  |  | 910-900 High Mass, S. Shade Cooling | -0.546 | -0.65436 | -0.453 | -0.81835 | -0.684 | -0.85903 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.682
296 | 3 | 24.9 | 26.66 | 23.4157 | 21.7632 | 22.68 | 21.2323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.83 |  |  |  | 620-600 Low Mass, E&W Or., Heating | -0.11 | 0.017627 | 0.033 | 0.024696 | 0.025 | 0.025699 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.05
297 | 4 | 24 | 26.1515 | 22.967 | 21.2816 | 22.16 | 20.7325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.33 |  |  |  | 620-600 Low Mass, E&W Or., Cooling | -0.946 | -1.9882 | -1.467 | -1.5541 | -1.571 | -1.4575 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.373
298 | 5 | 23.2 | 25.6862 | 22.6075 | 20.8555 | 21.69 | 20.2913 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20.95 |  |  |  | 920-900 High Mass, E&W Or., Heating | 0.344 | 0.069036 | 0.06 | 0.08269 | 0.073 | 0.085796 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.076
299 | 6 | 22.4 | 25.2544 | 22.1993 | 20.459 | 21.27 | 19.892 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20.51 |  |  |  | 920-900 HIgh Mass, E&W Or., Cooling | 0.442 | -0.31975 | 0.154 | 0.21988 | 0.203 | 0.21408 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.091
300 | 7 | 21.8 | 24.8308 | 21.8506 | 20.0788 | 20.84 | 19.4952 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20.15 |  |  |  | 630-620 Low Mass, E&W Shd., Heating | 0.107 | 0.001512 | 0.004 | -0.022564 | 0.006 | 0.0029619 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.006
301 | 8 | 21.4 | 24.9686 | 21.7274 | 20.2516 | 20.76 | 19.8079 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20.58 |  |  |  | 630-620 Low Mass, E&W Shd., Cooling | -0.583 | -0.49451 | -0.429 | -0.58526 | -0.651 | -0.63889 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.605
302 | 9 | 22 | 26.3146 | 22.6222 | 21.6585 | 21.86 | 21.363 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.34 |  |  |  | 930-920 High Mass, E&W Shd., Heating | 0.073 | 0.024542 | 0.036 | 0.014719 | 0.059 | 0.03614 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.033
303 | 10 | 23.5 | 28.2183 | 24.3831 | 23.5492 | 23.76 | 23.32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.4 |  |  |  | 930-920 High Mass, E&W Shd., Cooling | -0.429 | -0.39486 | -0.375 | -0.47881 | -0.605 | -0.54103 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.473
304 | 11 | 25.5 | 30.208 | 26.4423 | 25.5857 | 25.83 | 25.378 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 26.55
305 | 12 | 27.8 | 32.2226 | 28.5594 | 27.7875 | 28.05 | 27.6309 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.86
306 | 13 | 30.2 | 34.0812 | 30.5625 | 29.9726 | 30.34 | 29.7398 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30.93
307 | 14 | 32.3 | 35.3862 | 31.8566 | 31.4705 | 32.04 | 31.1593 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 31.79
308 | 15 | 33.8 | 35.9936 | 32.861 | 32.0838 | 32.66 | 31.7177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32.46 |  |  |  | BESTEST BASIC Thermostat, Ventilation and Sunspace (Delta) Annual Heating and Cooling
309 | 16 | 34.6 | 36.0431 | 33.2429 | 32.1996 | 32.9 | 31.761 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32.45 |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
310 | 17 | 34 | 35.2665 | 32.828 | 31.4583 | 32.38 | 30.9917 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 31.71 |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
311 | 18 | 32.9 | 33.6073 | 31.5769 | 29.8322 | 30.99 | 29.3415 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 29.97 |  |  |  | 640-600 Low Mass, Tstat Setback, Heating | -1.368 | -1.5895 | -1.428 | -1.6625 | -1.7076 | -1.8508 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -2.017
312 | 19 | 32 | 32.4976 | 30.4417 | 28.6662 | 29.68 | 28.1322 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.83 |  |  |  | 940-900 High Mass, Tstat Setback, Heating | -0.337 | -0.51566 | -0.442 | -0.5963 | -0.57 | -0.6449 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.6878
313 | 20 | 31.2 | 31.7818 | 29.6795 | 27.8593 | 28.9 | 27.3891 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27.97 |  |  |  | 650-600 Low Mass, Night Vent, Cooling | -1.193 | -1.2592 | -1.246 | -1.2103 | -1.2167 | -1.1472 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.1614
314 | 21 | 30.3 | 31.126 | 28.995 | 27.1608 | 28.17 | 26.6361 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27.3 |  |  |  | 950-900 High Mass, Night Vent, Cooling | -2.128 | -1.8658 | -1.765 | -1.7818 | -1.8317 | -1.6255 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.7097
315 | 22 | 29.4 | 30.5149 | 28.3418 | 26.4922 | 27.47 | 26.0008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 26.55 |  |  |  | 960-900 High Mass, Sunspace, Heating | #N/A | 1.1432 | 1.18 | 1.0254 | 1.0392 | 1.0455 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.2762
316 | 23 | 28.4 | 29.9001 | 27.7806 | 25.8183 | 26.76 | 25.3028 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.92 |  |  |  | 960-900 High Mass, Sunspace, Cooling | #N/A | -1.538 | -1.474 | -1.5816 | -1.5381 | -1.4782 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.6476
317 | 24 | 27.4 | 29.355 | 27.2948 | 25.2512 | 26.21 | 24.7283 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.38
| = | = | = | = | = | = | = | = | = | [8 empty] | =
BESTEST BASIC Thermostat, Ventilation and Sunspace (Delta) Peak Heating and Cooling
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | 640-600 Low Mass, Tstat Setback, Heating | 1.378 | 1.2022 | 1.623 | 1.3541 | 0.873 | 0.67965 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 1.102
[22 empty] | 940-900 High Mass, Tstat Setback, Heating | 1.331 | 0.60852 | 1.206 | 0.45528 | 0.489 | 0.62635 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: 0.807
[22 empty] | 650-600 Low Mass, Night Vent, Cooling | -0.002 | -0.19129 | -0.377 | -0.21342 | -0.232 | -0.24825 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.168
[22 empty] | 950-900 High Mass, Night Vent, Cooling | -0.673 | -1.0129 | -0.502 | -0.65292 | -0.694 | -0.70368 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.481
| FREE-FLOAT CASES | [20 empty] | 960-900 High Mass, Sunspace, Heating | #N/A | -0.31135 | -0.368 | -0.42812 | -0.432 | -0.47808 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -0.374
| HOURLY ANNUAL ZONE TEMPERATURE BIN DATA | [20 empty] | 960-900 High Mass, Sunspace, Cooling | #N/A | -1.9993 | -1.189 | -1.5605 | -1.493 | -1.6016 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: -1.46
CASE 900FF
(USE COLUMN B ONLY)
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
# HOURS | TEMP (C) | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS
| = | = | = | = | = | = | = | = | = | [8 empty] | =
330 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
331 | -49 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
332 | -48 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
333 | -47 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
334 | -46 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
335 | -45 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
336 | -44 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
337 | -43 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
338 | -42 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
339 | -41 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
340 | -40 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
341 | -39 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
342 | -38 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
343 | -37 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
344 | -36 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
345 | -35 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
346 | -34 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
347 | -33 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
348 | -32 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
349 | -31 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
350 | -30 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
351 | -29 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
352 | -28 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
353 | -27 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
354 | -26 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
355 | -25 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
356 | -24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
357 | -23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
358 | -22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
359 | -21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
360 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
361 | -19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
362 | -18 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
363 | -17 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
364 | -16 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
365 | -15 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
366 | -14 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
367 | -13 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
368 | -12 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
369 | -11 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
370 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
371 | -9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
372 | -8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
373 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
374 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
375 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
376 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
377 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
378 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
379 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
380 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2
381 | 1 | 13 | 0 | 3 | 4 | 3 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3
382 | 2 | 32 | 4 | 8 | 4 | 6 | 16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4
383 | 3 | 41 | 7 | 19 | 20 | 19 | 25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17
384 | 4 | 57 | 23 | 32 | 21 | 29 | 24 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 26
385 | 5 | 63 | 25 | 31 | 39 | 29 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 34
386 | 6 | 67 | 36 | 42 | 51 | 43 | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50
387 | 7 | 87 | 44 | 60 | 63 | 66 | 74 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 74
388 | 8 | 97 | 65 | 110 | 71 | 74 | 75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 73
389 | 9 | 104 | 74 | 95 | 83 | 96 | 102 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 99
390 | 10 | 155 | 98 | 112 | 128 | 110 | 142 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 125
391 | 11 | 151 | 117 | 155 | 164 | 141 | 184 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 167
392 | 12 | 142 | 148 | 190 | 218 | 200 | 212 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 202
393 | 13 | 156 | 211 | 230 | 185 | 203 | 192 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 208
394 | 14 | 170 | 206 | 229 | 197 | 196 | 204 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 200
395 | 15 | 166 | 208 | 244 | 253 | 238 | 289 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 263
396 | 16 | 211 | 255 | 291 | 269 | 271 | 255 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 284
397 | 17 | 199 | 288 | 297 | 241 | 271 | 278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 257
398 | 18 | 211 | 253 | 334 | 312 | 310 | 351 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 317
399 | 19 | 257 | 329 | 337 | 321 | 340 | 323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 333
400 | 20 | 318 | 365 | 313 | 337 | 323 | 317 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 314
401 | 21 | 263 | 323 | 324 | 305 | 319 | 326 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 307
402 | 22 | 269 | 327 | 267 | 324 | 319 | 306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 321
403 | 23 | 273 | 316 | 253 | 302 | 285 | 291 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 294
404 | 24 | 260 | 283 | 252 | 276 | 272 | 280 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 279
405 | 25 | 308 | 286 | 241 | 296 | 270 | 292 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 299
406 | 26 | 339 | 299 | 254 | 283 | 270 | 288 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 283
407 | 27 | 330 | 287 | 241 | 313 | 272 | 330 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 299
408 | 28 | 341 | 319 | 264 | 302 | 318 | 310 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315
409 | 29 | 409 | 340 | 297 | 326 | 296 | 356 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 335
410 | 30 | 382 | 362 | 298 | 356 | 327 | 383 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 370
411 | 31 | 426 | 417 | 331 | 386 | 363 | 385 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 383
412 | 32 | 433 | 429 | 377 | 366 | 374 | 411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 382
413 | 33 | 391 | 417 | 384 | 399 | 403 | 379 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 383
414 | 34 | 332 | 390 | 411 | 374 | 390 | 338 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 349
415 | 35 | 291 | 335 | 363 | 315 | 336 | 265 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 297
416 | 36 | 244 | 272 | 315 | 253 | 292 | 232 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 238
417 | 37 | 184 | 210 | 255 | 209 | 237 | 161 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 197
418 | 38 | 167 | 150 | 208 | 152 | 178 | 113 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 145
419 | 39 | 145 | 77 | 132 | 118 | 117 | 71 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 85
420 | 40 | 102 | 60 | 75 | 64 | 71 | 39 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 70
421 | 41 | 76 | 40 | 45 | 34 | 45 | 21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 38
422 | 42 | 41 | 30 | 24 | 17 | 21 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22
423 | 43 | 27 | 21 | 12 | 7 | 14 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11
424 | 44 | 22 | 11 | 5 | 2 | 3 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6
425 | 45 | 5 | 3 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
426 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
427 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
428 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
429 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
430 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
431 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
432 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
433 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
434 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
435 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
436 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
437 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
438 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
439 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
440 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
441 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
442 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
443 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
444 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
445 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
446 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
447 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
448 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
449 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
450 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
451 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
452 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
453 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
454 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
455 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
456 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
457 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
458 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
459 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
460 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
461 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
462 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
463 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
464 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
465 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
466 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
467 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
468 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
469 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
470 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
471 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
472 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
473 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
474 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
475 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
476 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
477 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
478 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = |  | ======== | = | = | [8 empty] | =
| = | = | = | = | = |  | ======== | = | = | [8 empty] | =
| = | = | = | = | = |  | = | = | = | [8 empty] | =
| = | = | = | = | = |  | = | = | = | [8 empty] | =
Data Tables for Figures 47 to 50 to allow Different labels for Series [Note (2019Aug01): Rows 1030 to 1050 appear to be orphaned, not used in charts]
Heating
0
0 | Heating | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
ref | 395 Low Mass Solid Conduction | 4.565 | 4.855 | 5.145 | 4.6412 | 4.8657 | 4.9081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.0113
ref | 430 Low Mass High Cond. Wall El. | 5.171 | 5.454 | 5.954 | 5.6201 | 5.5449 | 5.8505 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.9253
ref | 800 High Mass High Cond. Wall El. | 5.141 | 4.9057 | 5.403 | 5.1156 | 4.9798 | 5.3695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.4287
0 | Cooling | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
ref | 395 Low Mass Solid Conduction | 0.021 | 0.007762 | 0.006 | 0.01038 | 0.0055 | 0.0035162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0048
ref | 430 Low Mass High Cond. Wall El. | 1.084 | 0.90616 | 0.944 | 0.85562 | 0.9527 | 0.73902 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.7501
ref | 800 High Mass High Cond. Wall El. | 0.473 | 0.37983 | 0.362 | 0.37353 | 0.3914 | 0.28208 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2682
0 | Peak Heating | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
ref | 395 Low Mass Solid Conduction | 1.948 | 2.1574 | 2.085 | 1.9517 | 2.09 | 2.1613 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.04
ref | 430 Low Mass High Cond. Wall El. | 3.3 | 3.2539 | 3.36 | 3.3163 | 3.285 | 3.4088 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.283
ref | 800 High Mass High Cond. Wall El. | 2.957 | 2.7776 | 2.864 | 2.9237 | 2.84 | 2.9669 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.846
0 | Peak Cooling | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
ref | 395 Low Mass Solid Conduction | 0.547 | 0.3575 | 0.308 | 0.37747 | 0.294 | 0.2652 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.282
ref | 430 Low Mass High Cond. Wall El. | 2.167 | 1.8398 | 1.84 | 1.9294 | 1.874 | 1.7041 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.677
ref | 800 High Mass High Cond. Wall El. | 1.286 | 1.1019 | 1.157 | 1.0458 | 1.052 | 0.93559 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.016
MONTHLY HEATING & COOLING LOAD DATA
Case 600
Monthly Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 663.99 | 655.585 | 672.684 | 711.8797 | 732 | 734.943 | [10 empty] | 719.33
1 | Feb | 653.26 | 626.2627 | 635.299 | 682.632 | 682 | 702.079 | [10 empty] | 687.11
2 | Mar | 433.508 | 435.7419 | 450.494 | 472.2167 | 481 | 495.001 | [10 empty] | 493.74
3 | Apr | 511.036 | 456.9543 | 447.957 | 510.1244 | 479 | 517.287 | [10 empty] | 516.41
4 | May | 112.769 | 127.7958 | 128 | 136.8192 | 139 | 150.732 | [10 empty] | 156.11
5 | Jun | 2.735 | 11.6999 | 11.218 | 10.0812 | 14 | 15.9512 | [10 empty] | 18.4
6 | Jul | 4.839 | 11.5431 | 10.105 | 12.0182 | 14 | 16.7263 | [10 empty] | 18.44
7 | Aug | 1.368 | 6.9186 | 8.376 | 6.5877 | 9 | 9.6039 | [10 empty] | 11.83
8 | Sep | 51.756 | 74.3067 | 76.741 | 73.317 | 81 | 84.8239 | [10 empty] | 89.27
9 | Oct | 316.952 | 328.4088 | 324.148 | 347.7084 | 354 | 367.051 | [10 empty] | 363.1
10 | Nov | 598.664 | 575.553 | 585.805 | 625.2596 | 629 | 645.809 | [10 empty] | 632.65
11 | Dec | 698.704 | 681.9851 | 697.819 | 735.7303 | 750 | 763.546 | [10 empty] | 749.73
| sum | 4049.581 | 3992.755 | 4048.646 | 4324.3743 | 4364 | 4503.5533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 475.4 | 554.0235 | 417.93 | 521.798 | 523 | 495.012 | [10 empty] | 478.98
1 | Feb | 349.2 | 394.2972 | 315.415 | 387.4981 | 398 | 367.404 | [10 empty] | 360.93
2 | Mar | 450.3 | 474.3508 | 410.736 | 484.3611 | 489 | 457.384 | [10 empty] | 460.76
3 | Apr | 218.7 | 220.1356 | 230.168 | 240.4611 | 263 | 235.357 | [10 empty] | 240.77
4 | May | 342.7 | 321.1602 | 338.582 | 339.9139 | 364 | 325.154 | [10 empty] | 329.98
5 | Jun | 578.3 | 497.4498 | 526.439 | 539.605 | 550 | 516.057 | [10 empty] | 516.12
6 | Jul | 568.4 | 505.8671 | 525.149 | 536.3834 | 556 | 514.389 | [10 empty] | 517.58
7 | Aug | 658.2 | 606.5032 | 621.101 | 648.5013 | 674 | 634.136 | [10 empty] | 645.94
8 | Sep | 724.8 | 705.1929 | 672.084 | 733.708 | 743 | 710.474 | [10 empty] | 727.97
9 | Oct | 628.4 | 676.133 | 611.126 | 675.2687 | 681 | 649.483 | [10 empty] | 654.28
10 | Nov | 394.3 | 454.7409 | 377.147 | 437.6814 | 444 | 418.571 | [10 empty] | 413.33
11 | Dec | 433.3 | 503.27 | 386.209 | 481.8594 | 476 | 456.103 | [10 empty] | 443.2
| sum | 5822 | 5913.1242 | 5432.086 | 6027.0394 | 6161 | 5779.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 3.1 | 3.0202 | 3.036 | 2.9776 | 3.23 | 3.3589 | [10 empty] | 2.999
1 | Feb | 3.041 | 2.8997 | 2.922 | 3.0666 | 3.14 | 3.2252 | [10 empty] | 3.13
2 | Mar | 2.275 | 2.0344 | 2.065 | 2.1146 | 2.23 | 2.287 | [10 empty] | 2.274
3 | Apr | 2.446 | 2.2073 | 2.238 | 2.3223 | 2.38 | 2.4572 | [10 empty] | 2.408
4 | May | 1.645 | 1.5922 | 1.569 | 1.6241 | 1.75 | 1.778 | [10 empty] | 1.746
5 | Jun | 0.805 | 0.77848 | 0.748 | 0.73243 | 0.76 | 0.8526 | [10 empty] | 0.905
6 | Jul | 0.599 | 0.53975 | 0.512 | 0.51445 | 0.57 | 0.61893 | [10 empty] | 0.673
7 | Aug | 0.572 | 0.55338 | 0.532 | 0.47852 | 0.56 | 0.59085 | [10 empty] | 0.624
8 | Sep | 1.229 | 1.1204 | 1.114 | 1.1295 | 1.19 | 1.2116 | [10 empty] | 1.232
9 | Oct | 1.702 | 1.6237 | 1.619 | 1.682 | 1.77 | 1.8132 | [10 empty] | 1.772
10 | Nov | 3.255 | 2.8502 | 2.931 | 3.1061 | 3.11 | 3.2066 | [10 empty] | 3.117
11 | Dec | 3.171 | 2.9413 | 2.972 | 3.2044 | 3.17 | 3.2781 | [10 empty] | 3.198
| max | 3.255 | 3.0202 | 3.036 | 3.2044 | 3.23 | 3.3589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 5.65 | 6.481 | 5.422 | 6.3516 | 6.19 | 6.0457 | [10 empty] | 5.523
1 | Feb | 4.9211 | 5.3928 | 4.444 | 5.5373 | 5.42 | 5.1553 | [10 empty] | 4.798
2 | Mar | 4.4579 | 5.1483 | 4.252 | 5.0085 | 5.04 | 4.7399 | [10 empty] | 4.402
3 | Apr | 3.4735 | 4.0151 | 3.6 | 3.9307 | 4.04 | 3.8027 | [10 empty] | 3.65
4 | May | 2.7741 | 3.0796 | 2.894 | 3.0864 | 3.1 | 3.0405 | [10 empty] | 2.899
5 | Jun | 3.2526 | 3.2488 | 3.067 | 3.4487 | 3.43 | 3.3792 | [10 empty] | 3.22
6 | Jul | 3.3187 | 3.2903 | 3.155 | 3.6284 | 3.64 | 3.4967 | [10 empty] | 3.409
7 | Aug | 4.1922 | 4.1195 | 4.038 | 4.672 | 4.7 | 4.6505 | [10 empty] | 4.414
8 | Sep | 5.086 | 5.4503 | 4.911 | 5.7148 | 5.58 | 5.4199 | [10 empty] | 5.18
9 | Oct | 5.5767 | 6.2702 | 5.278 | 6.2221 | 6.07 | 5.9226 | [10 empty] | 5.609
10 | Nov | 5.4759 | 6.149 | 5.229 | 6.194 | 6.03 | 5.824 | [10 empty] | 5.407
11 | Dec | 5.537 | 6.45 | 5.294 | 6.251 | 6.12 | 5.9425 | [10 empty] | 5.45
| max | 5.65 | 6.481 | 5.422 | 6.3516 | 6.19 | 6.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Case 900
Monthly Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 277.8 | 206.1043 | 275.307 | 255.8355 | 266 | 291.936 | [10 empty] | 282.23
1 | Feb | 307.4 | 243.2297 | 292.916 | 294.1814 | 283 | 322.141 | [10 empty] | 312.77
2 | Mar | 134.4 | 102.4399 | 119.976 | 125.5424 | 115 | 143.84 | [10 empty] | 140.44
3 | Apr | 275.7 | 222.3692 | 214.166 | 268.6543 | 228 | 275.466 | [10 empty] | 271.95
4 | May | 20.1 | 33.3469 | 26.771 | 33.4139 | 29 | 37.5028 | [10 empty] | 35.54
5 | Jun | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0
6 | Jul | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0
7 | Aug | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0
8 | Sep | 2.1 | 0 | 0 | 0.11241 | 0 | 0.53697 | [10 empty] | 0.3
9 | Oct | 80.5 | 65.0694 | 63.591 | 81.0905 | 70 | 85.0098 | [10 empty] | 81.19
10 | Nov | 298.2 | 251.5988 | 283.888 | 296.9874 | 286 | 318.242 | [10 empty] | 308.36
11 | Dec | 329.8 | 254.733 | 314.279 | 307.8688 | 308 | 339.357 | [10 empty] | 332.3
| sum | 1726 | 1378.8913 | 1590.894 | 1663.6867 | 1585 | 1814.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 73.3141 | 67.8041 | 33.493 | 53.2805 | 42 | 44.635 | [10 empty] | 53.11
1 | Feb | 24.0087 | 15.1117 | 4.724 | 12.3391 | 11 | 9.2434 | [10 empty] | 13.47
2 | Mar | 86.3882 | 68.5488 | 40.898 | 65.3862 | 56 | 50.5508 | [10 empty] | 65.77
3 | Apr | 29.344 | 12.3134 | 18.267 | 18.4694 | 22 | 16.0525 | [10 empty] | 21.99
4 | May | 131.0941 | 117.8126 | 128.592 | 114.4874 | 125 | 98.3549 | [10 empty] | 107.69
5 | Jun | 447.4956 | 372.2992 | 408.473 | 401.3344 | 404 | 365.819 | [10 empty] | 378.33
6 | Jul | 440.8962 | 380.4363 | 408.145 | 398.7064 | 410 | 365.513 | [10 empty] | 382.01
7 | Aug | 532.6434 | 485.6761 | 510.152 | 510.3174 | 531 | 487.566 | [10 empty] | 517.28
8 | Sep | 517.8661 | 484.0294 | 466.106 | 492.837 | 492 | 458.859 | [10 empty] | 500.2
9 | Oct | 296.188 | 305.5693 | 269.566 | 292.6655 | 281 | 260.853 | [10 empty] | 292.83
10 | Nov | 72.6701 | 80.4854 | 56.214 | 67.9828 | 63 | 60.1796 | [10 empty] | 70.48
11 | Dec | 62.0916 | 73.7394 | 38.054 | 60.9353 | 48 | 49.5012 | [10 empty] | 57.43
| sum | 2714 | 2463.8258 | 2382.684 | 2488.7414 | 2485 | 2267.1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 2.322 | 2.0774 | 2.178 | 1.9028 | 2.2 | 2.3786 | [10 empty] | 1.968
1 | Feb | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.63 | 2.7785 | [10 empty] | 2.672
2 | Mar | 1.774 | 1.6129 | 1.646 | 1.7443 | 1.76 | 1.8582 | [10 empty] | 1.847
3 | Apr | 1.997 | 1.7706 | 1.725 | 2.0036 | 1.93 | 2.0359 | [10 empty] | 1.981
4 | May | 1.295 | 1.1425 | 1.124 | 1.2682 | 1.23 | 1.3242 | [10 empty] | 1.315
5 | Jun | 0 | 0 |  | 0 | 0 | 0 | [10 empty] | 0
6 | Jul | 0 | 0 |  | 0 | 0 | 0 | [10 empty] | 0
7 | Aug | 0 | 0 |  | 0 | 0 | 0 | [10 empty] | 0
8 | Sep | 0.113 | 0 |  | 0.064157 | 0 | 0.19442 | [10 empty] | 0.152
9 | Oct | 1.201 | 1.1882 | 1.158 | 1.3258 | 1.21 | 1.3311 | [10 empty] | 1.312
10 | Nov | 2.427 | 2.0863 | 2.201 | 2.3161 | 2.28 | 2.4629 | [10 empty] | 2.394
11 | Dec | 2.12 | 1.9268 | 1.981 | 2.1749 | 2.04 | 2.1801 | [10 empty] | 2.136
| max | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.63 | 2.7785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 1.982 | 2.2416 | 1.637 | 2.0779 | 1.81 | 1.8776 | [10 empty] | 1.932
1 | Feb | 1.096 | 0.99617 | 0.588 | 0.97943 | 0.85 | 0.82938 | [10 empty] | 1.03
2 | Mar | 1.508 | 1.4341 | 1.143 | 1.4931 | 1.27 | 1.4258 | [10 empty] | 1.637
3 | Apr | 1.093 | 0.63116 | 1.032 | 0.95262 | 0.95 | 0.83719 | [10 empty] | 1.073
4 | May | 1.555 | 1.4272 | 1.446 | 1.5339 | 1.46 | 1.4645 | [10 empty] | 1.532
5 | Jun | 2.101 | 1.8967 | 1.873 | 1.9656 | 1.89 | 1.9742 | [10 empty] | 1.912
6 | Jul | 2.14 | 1.943 | 1.83 | 2.0681 | 1.97 | 1.975 | [10 empty] | 2.022
7 | Aug | 2.632 | 2.4852 | 2.212 | 2.5258 | 2.51 | 2.5337 | [10 empty] | 2.484
8 | Sep | 2.961 | 3.1368 | 2.556 | 2.9888 | 2.81 | 2.8712 | [10 empty] | 2.818
9 | Oct | 3.039 | 3.3764 | 2.549 | 3.0404 | 2.9 | 2.9401 | [10 empty] | 2.785
10 | Nov | 1.982 | 2.2328 | 1.683 | 2.0018 | 1.94 | 1.9406 | [10 empty] | 1.978
11 | Dec | 2.069 | 2.1054 | 1.595 | 1.9682 | 1.67 | 1.6903 | [10 empty] | 1.781
| max | 3.039 | 3.3764 | 2.556 | 3.0404 | 2.9 | 2.9401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Case 600-900
Monthly Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 386.19 | 449.4807 | 397.377 | 456.0442 | 466 | 443.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437.1
1 | Feb | 345.86 | 383.033 | 342.383 | 388.4505 | 399 | 379.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374.34
2 | Mar | 299.108 | 333.302 | 330.518 | 346.6743 | 366 | 351.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353.3
3 | Apr | 235.336 | 234.5851 | 233.791 | 241.4701 | 251 | 241.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244.46
4 | May | 92.669 | 94.449 | 101.229 | 103.4052 | 110 | 113.2292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.57
5 | Jun | 2.735 | 11.6999 | 11.218 | 10.0812 | 14 | 15.9512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4
6 | Jul | 4.839 | 11.5431 | 10.105 | 12.0182 | 14 | 16.7263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.44
7 | Aug | 1.368 | 6.9186 | 8.376 | 6.5877 | 9 | 9.6039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.83
8 | Sep | 49.656 | 74.3067 | 76.741 | 73.2046 | 81 | 84.2869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.97
9 | Oct | 236.452 | 263.3394 | 260.557 | 266.6179 | 284 | 282.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281.91
10 | Nov | 300.464 | 323.9542 | 301.917 | 328.2722 | 343 | 327.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.29
11 | Dec | 368.904 | 427.2521 | 383.54 | 427.8615 | 442 | 424.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.43
Monthly Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 402.0859 | 486.2194 | 384.437 | 468.5175 | 481 | 450.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425.87
1 | Feb | 325.1913 | 379.1855 | 310.691 | 375.159 | 387 | 358.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347.46
2 | Mar | 363.9118 | 405.8019 | 369.838 | 418.9749 | 433 | 406.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394.99
3 | Apr | 189.356 | 207.8222 | 211.901 | 221.9916 | 241 | 219.3045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218.78
4 | May | 211.6059 | 203.3476 | 209.99 | 225.4265 | 239 | 226.7991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222.29
5 | Jun | 130.8044 | 125.1506 | 117.966 | 138.2706 | 146 | 150.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.79
6 | Jul | 127.5038 | 125.4308 | 117.004 | 137.6771 | 146 | 148.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135.57
7 | Aug | 125.5566 | 120.8271 | 110.949 | 138.1839 | 143 | 146.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128.66
8 | Sep | 206.9339 | 221.1635 | 205.978 | 240.871 | 251 | 251.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.77
9 | Oct | 332.212 | 370.5637 | 341.56 | 382.6032 | 400 | 388.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361.45
10 | Nov | 321.6299 | 374.2554 | 320.933 | 369.6986 | 381 | 358.3914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342.85
11 | Dec | 371.2084 | 429.5306 | 348.155 | 420.9241 | 428 | 406.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385.77
Monthly Peak Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 0.778 | 0.94282 | 0.858 | 1.0748 | 1.03 | 0.98026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.031
1 | Feb | 0.49 | 0.45628 | 0.469 | 0.37915 | 0.51 | 0.4467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.458
2 | Mar | 0.501 | 0.42158 | 0.419 | 0.37021 | 0.47 | 0.42882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.427
3 | Apr | 0.449 | 0.43669 | 0.513 | 0.31865 | 0.45 | 0.42125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.427
4 | May | 0.35 | 0.44976 | 0.445 | 0.35588 | 0.52 | 0.45382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.431
5 | Jun | 0.805 | 0.77848 | 0.748 | 0.73243 | 0.76 | 0.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.905
6 | Jul | 0.599 | 0.53975 | 0.512 | 0.51445 | 0.57 | 0.61893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.673
7 | Aug | 0.572 | 0.55338 | 0.532 | 0.47852 | 0.56 | 0.59085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.624
8 | Sep | 1.116 | 1.1204 | 1.114 | 1.0654 | 1.19 | 1.0172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08
9 | Oct | 0.501 | 0.43546 | 0.461 | 0.35615 | 0.56 | 0.4821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46
10 | Nov | 0.828 | 0.76387 | 0.73 | 0.78997 | 0.83 | 0.74371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.723
11 | Dec | 1.051 | 1.0145 | 0.991 | 1.0296 | 1.13 | 1.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.062
Monthly Peak Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 3.668 | 4.2394 | 3.785 | 4.2737 | 4.38 | 4.1681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.591
1 | Feb | 3.8251 | 4.3966 | 3.856 | 4.5578 | 4.57 | 4.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.768
2 | Mar | 2.9499 | 3.7143 | 3.109 | 3.5155 | 3.77 | 3.3142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.765
3 | Apr | 2.3805 | 3.3839 | 2.568 | 2.9781 | 3.09 | 2.9655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.577
4 | May | 1.2191 | 1.6524 | 1.448 | 1.5525 | 1.64 | 1.5759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.367
5 | Jun | 1.1516 | 1.3521 | 1.194 | 1.4832 | 1.54 | 1.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.308
6 | Jul | 1.1787 | 1.3473 | 1.325 | 1.5603 | 1.67 | 1.5217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.387
7 | Aug | 1.5602 | 1.6343 | 1.826 | 2.1462 | 2.19 | 2.1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.93
8 | Sep | 2.125 | 2.3135 | 2.355 | 2.726 | 2.77 | 2.5488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.362
9 | Oct | 2.5377 | 2.8938 | 2.729 | 3.1817 | 3.17 | 2.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.824
10 | Nov | 3.4939 | 3.9162 | 3.546 | 4.1922 | 4.09 | 3.8834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.429
11 | Dec | 3.468 | 4.3446 | 3.699 | 4.2828 | 4.45 | 4.2521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.669
HOURLY HEATING & COOLING LOAD DATA
CASE 600 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 2.032 | 1.8838 | 1.9869 | 2.1523 | 2.08 | 2.1718 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.1929
263 | 2 | 2.042 | 1.9935 | 2.0692 | 2.2223 | 2.22 | 2.271 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.2442
264 | 3 | 2.123 | 2.0547 | 2.1291 | 2.2757 | 2.3 | 2.3414 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.314
265 | 4 | 2.228 | 2.1202 | 2.2065 | 2.3283 | 2.38 | 2.4106 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.3793
266 | 5 | 2.307 | 2.1532 | 2.243 | 2.351 | 2.42 | 2.4393 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.3696
267 | 6 | 2.358 | 2.1631 | 2.2675 | 2.3515 | 2.43 | 2.4505 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4058
268 | 7 | 2.385 | 2.1843 | 2.2778 | 2.3551 | 2.46 | 2.4648 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4041
269 | 8 | 2.101 | 1.7765 | 2.1196 | 1.8832 | 2.09 | 1.7476 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7593
270 | 9 | 1.048 | 0.5478 | 1.2032 | 0.49397 | 0.79 | 0.29604 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1724
271 | 10 | 0.139 | 0 | 0 | 0 | 0 | -0.15773 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
272 | 11 | -0.07 | -0.92066 | -0.3574 | -1.3089 | -1.28 | -1.3665 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4371
273 | 12 | -1.616 | -3.0739 | -2.2142 | -3.4074 | -3.36 | -3.2336 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.0461
274 | 13 | -3.561 | -4.364 | -3.4723 | -4.6741 | -4.69 | -4.4188 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.0618
275 | 14 | -4.028 | -4.6667 | -4.0214 | -4.9334 | -5.08 | -4.5996 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.0489
276 | 15 | -3.839 | -4.0529 | -4.0239 | -4.1722 | -4.39 | -3.9649 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.7032
277 | 16 | -3.244 | -2.8873 | -3.4753 | -2.9277 | -3.24 | -2.8274 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.8273
278 | 17 | -2.197 | -1.329 | -2.3221 | -1.2391 | -1.59 | -1.1647 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4778
279 | 18 | -0.779 | -0.036587 | -0.6489 | -0.019928 | -0.12 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
280 | 19 | 0 | 0.047689 | 0 | 0.086501 | 0.1 | 0.36036 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
281 | 20 | 0 | 0.87302 | 0.1486 | 0.98137 | 1 | 1.0287 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8846
282 | 21 | 0.413 | 1.5518 | 1.0979 | 1.6393 | 1.7 | 1.6719 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.6036
283 | 22 | 1.266 | 1.9363 | 1.6738 | 2.0595 | 2.1 | 2.1066 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.054
284 | 23 | 1.814 | 2.1702 | 2.0148 | 2.3234 | 2.36 | 2.3929 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.2958
285 | 24 | 1.988 | 2.2658 | 2.1963 | 2.4352 | 2.47 | 2.5229 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4084
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 600 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
266 | 5 | 0 | 0 | 0 | 0 | 0.04 | 0.094557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1641
267 | 6 | 0 | 0 | 0 | 0 | 0.09 | 0.038588 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
269 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
270 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
271 | 10 | -0.332 | -0.16869 | -0.0988 | -0.35948 | -0.23 | -0.36749 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.574
272 | 11 | -1.246 | -1.2347 | -1.022 | -1.4584 | -1.21 | -1.2888 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.633
273 | 12 | -2.078 | -2.2634 | -1.7729 | -2.4228 | -2.22 | -2.1777 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.2299
274 | 13 | -2.457 | -2.7049 | -2.3147 | -2.8449 | -2.78 | -2.6489 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.6222
275 | 14 | -2.618 | -2.7504 | -2.5989 | -2.9085 | -2.93 | -2.7498 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.7062
276 | 15 | -2.588 | -2.449 | -2.594 | -2.641 | -2.72 | -2.5224 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.5424
277 | 16 | -2.388 | -1.9631 | -2.3269 | -2.2096 | -2.33 | -2.0736 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.0971
278 | 17 | -2.096 | -1.5159 | -1.9515 | -1.7631 | -1.88 | -1.6698 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.7004
279 | 18 | -1.763 | -1.1667 | -1.5665 | -1.37 | -1.49 | -1.3003 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.3143
280 | 19 | -1.404 | -0.84578 | -1.1763 | -0.98285 | -1.1 | -0.91574 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.925
281 | 20 | -0.995 | -0.48174 | -0.7328 | -0.56694 | -0.64 | -0.50284 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4668
282 | 21 | -0.593 | -0.1626 | -0.2983 | -0.231 | -0.24 | -0.19628 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.1374
283 | 22 | -0.32 | -0.010249 | -0.0186 | -0.04743 | -0.04 | -0.0091138 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
284 | 23 | -0.138 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
285 | 24 | -0.027 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 900 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0.792 | 0.71655 | 1.0685 | 0.97734 | 0.91 | 1.0334 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.1045
263 | 2 | 0.928 | 0.84236 | 1.1715 | 1.0829 | 1.06 | 1.1534 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2124
264 | 3 | 1.063 | 0.94623 | 1.2675 | 1.1826 | 1.17 | 1.2628 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.3311
265 | 4 | 1.187 | 1.0458 | 1.3715 | 1.2862 | 1.27 | 1.3755 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4429
266 | 5 | 1.296 | 1.1187 | 1.4399 | 1.366 | 1.36 | 1.4592 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5009
267 | 6 | 1.412 | 1.1879 | 1.5162 | 1.4385 | 1.43 | 1.5326 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5899
268 | 7 | 1.54 | 1.2589 | 1.5722 | 1.5049 | 1.51 | 1.6045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.6446
269 | 8 | 1.45 | 1.0863 | 1.5519 | 1.3243 | 1.42 | 1.3557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4063
270 | 9 | 0.724 | 0.53703 | 1.1996 | 0.79271 | 0.93 | 0.77638 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.736
271 | 10 | 0.149 | 0.11777 | 0.58712 | 0.26716 | 0.38 | 0.24812 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0564
272 | 11 | 0 | 0 | 0 | 0 | 0.01 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
273 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
274 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
275 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
276 | 15 | -0.128 | -0.02487 | 0 | -0.046329 | -0.06 | -0.0097877 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0765
277 | 16 | -0.128 | -0.0054093 | 0 | -0.027472 | -0.08 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0041
278 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
279 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
280 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
281 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
282 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
283 | 22 | 0 | 0 | 0 | 0 | 0 | 0.096471 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
284 | 23 | 0.183 | 0.081877 | 0.040877 | 0.17522 | 0.05 | 0.30642 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2729
285 | 24 | 0.342 | 0.29481 | 0.24467 | 0.39699 | 0.28 | 0.52323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.4632
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 900 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.223 | -0.052736 | -0.11986 | -0.10115 | -0.17 | -0.030013 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
263 | 2 | -0.069 | -0.0012209 | -0.038655 | -0.030142 | -0.09 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
264 | 3 | -0.012 | 0 | 0 | 0 | -0.01 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
266 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
267 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
269 | 8 | 0 | 0 | 0 | -0.016529 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
270 | 9 | -0.128 | -0.070157 | -0.11228 | -0.15912 | -0.11 | -0.090224 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.1172
271 | 10 | -0.453 | -0.36695 | -0.36477 | -0.41739 | -0.31 | -0.31161 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.509
272 | 11 | -0.771 | -0.76666 | -0.66069 | -0.76505 | -0.61 | -0.65319 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.9139
273 | 12 | -1.234 | -1.1411 | -0.94273 | -1.1012 | -0.94 | -0.9806 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1701
274 | 13 | -1.545 | -1.3558 | -1.1934 | -1.3309 | -1.21 | -1.22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.3903
275 | 14 | -1.667 | -1.4518 | -1.3604 | -1.4697 | -1.38 | -1.3604 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4891
276 | 15 | -1.652 | -1.3908 | -1.413 | -1.4822 | -1.44 | -1.3762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4777
277 | 16 | -1.581 | -1.2243 | -1.3583 | -1.399 | -1.38 | -1.275 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.327
278 | 17 | -1.472 | -1.0839 | -1.2639 | -1.291 | -1.3 | -1.1791 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2085
279 | 18 | -1.343 | -0.97268 | -1.1433 | -1.1649 | -1.2 | -1.0627 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0665
280 | 19 | -1.201 | -0.8477 | -1.0072 | -1.0134 | -1.07 | -0.91459 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.9133
281 | 20 | -1.018 | -0.71147 | -0.84822 | -0.84554 | -0.92 | -0.75544 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.7291
282 | 21 | -0.832 | -0.58603 | -0.70104 | -0.70239 | -0.77 | -0.62069 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5886
283 | 22 | -0.661 | -0.48581 | -0.59136 | -0.59073 | -0.65 | -0.50904 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4882
284 | 23 | -0.492 | -0.39359 | -0.48628 | -0.48864 | -0.54 | -0.40721 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3778
285 | 24 | -0.371 | -0.28879 | -0.37086 | -0.37539 | -0.42 | -0.29064 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2453
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 640 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0.00043451 | 0.025 | 0.082706 | 0.08 | 0.11565 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1977
263 | 2 | 0 | 0.39261 | 0.611 | 0.54755 | 0.6 | 0.62194 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.7636
264 | 3 | 0.459 | 0.80293 | 0.951 | 0.91754 | 0.99 | 0.95848 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0729
265 | 4 | 1.053 | 1.034 | 1.19 | 1.1473 | 1.21 | 1.1918 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2776
266 | 5 | 1.231 | 1.1731 | 1.321 | 1.2747 | 1.35 | 1.3222 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.3508
267 | 6 | 1.272 | 1.2448 | 1.402 | 1.3397 | 1.42 | 1.4041 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4438
268 | 7 | 1.306 | 1.3018 | 1.445 | 1.3839 | 1.48 | 1.466 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4769
269 | 8 | 3.487 | 3.0205 | 3.844 | 3.3808 | 3.06 | 2.5037 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8482
270 | 9 | 3.024 | 1.6521 | 2.167 | 1.7525 | 1.94 | 1.4631 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.0555
271 | 10 | 0.185 | 0.075395 | 0.159 | 0.053533 | 0.15 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
272 | 11 | -0.068 | -0.40515 | 0 | -0.67412 | -0.7 | -1.0953 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6027
273 | 12 | -1.581 | -2.6298 | -1.927 | -3.0125 | -2.96 | -2.69 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.6254
274 | 13 | -3.487 | -4.1733 | -3.305 | -4.5085 | -4.51 | -4.1451 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.8107
275 | 14 | -3.945 | -4.592 | -3.923 | -4.868 | -5 | -4.4711 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.8987
276 | 15 | -3.759 | -4.0239 | -3.966 | -4.1472 | -4.36 | -3.9067 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.6131
277 | 16 | -3.243 | -2.8759 | -3.441 | -2.918 | -3.23 | -2.8007 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.7731
278 | 17 | -2.215 | -1.3246 | -2.302 | -1.2353 | -1.59 | -1.1527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.445
279 | 18 | -0.786 | -0.036104 | -0.637 | -0.019589 | -0.1 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
280 | 19 | 0 | 0.048108 | 0 | 0.087045 | 0.1 | 0.36164 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
281 | 20 | 0 | 0.87401 | 0.155 | 0.98216 | 1 | 1.0323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9017
282 | 21 | 0.401 | 1.5523 | 1.102 | 1.6398 | 1.7 | 1.6738 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.6121
283 | 22 | 1.239 | 1.9366 | 1.676 | 2.0598 | 2.1 | 2.1079 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.0591
284 | 23 | 1.781 | 2.1703 | 2.016 | 2.3235 | 2.36 | 2.3936 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.2988
285 | 24 | 0.082 | 0 | 0 | 0 | 0.32 | 0.8527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 660 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 1.803 | 1.6843 | 1.835 | 1.8505 | 1.79 | 1.8233 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.9142
263 | 2 | 1.782 | 1.779 | 1.901 | 1.9038 | 1.89 | 1.8954 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.9489
264 | 3 | 1.82 | 1.8309 | 1.95 | 1.9434 | 1.94 | 1.9466 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.9975
265 | 4 | 1.881 | 1.8839 | 2.017 | 1.9828 | 2 | 1.9958 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.046
266 | 5 | 1.923 | 1.9135 | 2.048 | 1.9989 | 2.04 | 2.0162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.035
267 | 6 | 1.952 | 1.9223 | 2.071 | 2.0006 | 2.05 | 2.028 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.0704
268 | 7 | 1.969 | 1.9415 | 2.078 | 2.0091 | 2.08 | 2.0459 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.0715
269 | 8 | 1.804 | 1.6726 | 1.966 | 1.7123 | 1.86 | 1.6135 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.6575
270 | 9 | 1.191 | 0.80151 | 1.334 | 0.82326 | 1.01 | 0.71656 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.6446
271 | 10 | 0.37 | 0.082875 | 0.264 | 0.061784 | 0.13 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
272 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
273 | 12 | 0 | -0.45456 | -0.147 | -0.49567 | -0.47 | -0.52411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.7653
274 | 13 | -0.545 | -1.6509 | -1.232 | -1.6957 | -1.63 | -1.5139 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.695
275 | 14 | -1.376 | -2.1461 | -1.705 | -2.1841 | -2.18 | -1.8748 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.7558
276 | 15 | -1.55 | -1.9151 | -1.796 | -1.8726 | -1.95 | -1.6375 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.596
277 | 16 | -1.192 | -1.281 | -1.52 | -1.2021 | -1.37 | -1.0626 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0834
278 | 17 | -0.576 | -0.38043 | -0.843 | -0.29981 | -0.49 | -0.18596 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2583
279 | 18 | -0.102 | 0 | 0 | 0 | -0.02 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
280 | 19 | 0 | 0.068677 | 0 | 0.10283 | 0.08 | 0.24487 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1165
281 | 20 | 0.061 | 0.85087 | 0.486 | 0.84738 | 0.87 | 0.90071 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0233
282 | 21 | 0.76 | 1.4115 | 1.198 | 1.4079 | 1.46 | 1.4225 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5505
283 | 22 | 1.518 | 1.7543 | 1.641 | 1.7785 | 1.81 | 1.792 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.8786
284 | 23 | 1.701 | 1.9598 | 1.904 | 2.0051 | 2.03 | 2.0235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.0521
285 | 24 | 1.801 | 2.0439 | 2.043 | 2.1 | 2.13 | 2.1255 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.1258
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 660 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
266 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
267 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
269 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
270 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
271 | 10 | -0.141 | -0.059292 | 0 | -0.16326 | -0.08 | -0.17059 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2135
272 | 11 | -0.797 | -0.78553 | -0.775 | -0.88657 | -0.65 | -0.72317 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0738
273 | 12 | -1.474 | -1.5756 | -1.407 | -1.5988 | -1.38 | -1.35 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4995
274 | 13 | -1.707 | -1.9242 | -1.85 | -1.9127 | -1.81 | -1.6997 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.7842
275 | 14 | -1.809 | -2.0023 | -2.099 | -2.0065 | -1.97 | -1.8273 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8732
276 | 15 | -1.824 | -1.8527 | -2.135 | -1.9013 | -1.92 | -1.7611 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8252
277 | 16 | -1.741 | -1.5702 | -1.953 | -1.6894 | -1.75 | -1.5425 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.5703
278 | 17 | -1.567 | -1.2726 | -1.664 | -1.4112 | -1.49 | -1.3035 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.3145
279 | 18 | -1.335 | -1.0133 | -1.354 | -1.1343 | -1.23 | -1.0574 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0463
280 | 19 | -1.08 | -0.76378 | -1.034 | -0.84941 | -0.95 | -0.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.7624
281 | 20 | -0.775 | -0.45877 | -0.657 | -0.52226 | -0.59 | -0.46077 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4028
282 | 21 | -0.461 | -0.17946 | -0.275 | -0.24015 | -0.24 | -0.21189 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.136
283 | 22 | -0.247 | -0.026977 | -0.028 | -0.081429 | -0.07 | -0.05591 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
284 | 23 | -0.107 | 0 | 0 | -0.0055834 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
285 | 24 | -0.022 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 670 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 2.67 | 2.3394 | 2.545 | 2.6246 | 2.68 | 2.7706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.7005
263 | 2 | 2.694 | 2.4806 | 2.631 | 2.7315 | 2.95 | 2.9307 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.7803
264 | 3 | 2.819 | 2.5674 | 2.707 | 2.8196 | 3.1 | 3.0517 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.8921
265 | 4 | 2.973 | 2.6744 | 2.81 | 2.9079 | 3.24 | 3.1786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.9948
266 | 5 | 3.088 | 2.7158 | 2.851 | 2.9498 | 3.31 | 3.2358 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.9914
267 | 6 | 3.145 | 2.7285 | 2.88 | 2.9434 | 3.31 | 3.2352 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.0123
268 | 7 | 3.154 | 2.7542 | 2.899 | 2.9242 | 3.3 | 3.2195 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.996
269 | 8 | 2.796 | 2.2606 | 2.693 | 2.3743 | 2.84 | 2.3857 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.2917
270 | 9 | 1.524 | 0.84369 | 1.593 | 0.72924 | 1.21 | 0.68716 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.5202
271 | 10 | 0.298 | 0.0024258 | 0 | 0 | 0.02 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
272 | 11 | 0 | -0.99799 | -0.306 | -1.2959 | -1.14 | -1.2316 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0569
273 | 12 | -1.564 | -3.2655 | -2.277 | -3.5295 | -3.35 | -3.1719 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.8741
274 | 13 | -3.679 | -4.6214 | -3.608 | -4.9384 | -4.86 | -4.5095 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.9942
275 | 14 | -4.214 | -4.8903 | -4.154 | -5.1408 | -5.1 | -4.5907 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.771
276 | 15 | -3.989 | -4.1429 | -4.118 | -4.1667 | -3.94 | -3.7353 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.3513
277 | 16 | -3.33 | -2.8645 | -3.498 | -2.7773 | -2.63 | -2.4556 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.4158
278 | 17 | -2.176 | -1.1447 | -2.216 | -0.98623 | -0.94 | -0.70988 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0962
279 | 18 | -0.736 | 0 | -0.314 | 0 | -0.02 | 0.1031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
280 | 19 | 0 | 0.3733 | 0 | 0.4619 | 0.72 | 0.78486 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.392
281 | 20 | 0.146 | 1.5232 | 0.909 | 1.6223 | 1.84 | 1.8058 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.6082
282 | 21 | 1.072 | 2.1392 | 1.818 | 2.2179 | 2.4 | 2.3956 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.156
283 | 22 | 2.06 | 2.4968 | 2.378 | 2.6015 | 2.75 | 2.8009 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.6283
284 | 23 | 2.396 | 2.7218 | 2.707 | 2.8785 | 3.03 | 3.1203 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.8758
285 | 24 | 2.613 | 2.8049 | 2.874 | 2.9941 | 3.11 | 3.2615 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.9932
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 670 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
265 | 4 | 0 | 0.001611 | 0.131 | 0 | 0.12 | 0.13713 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2699
266 | 5 | 0 | 0.20148 | 0.363 | 0.11574 | 0.33 | 0.32542 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.4714
267 | 6 | 0 | 0.20839 | 0.33 | 0.10059 | 0.29 | 0.22218 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1898
268 | 7 | 0 | 0.0044408 | 0.012 | 0 | 0.02 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
269 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
270 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
271 | 10 | -0.324 | -0.19006 | -0.047 | -0.42413 | -0.26 | -0.44642 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6273
272 | 11 | -1.402 | -1.5089 | -1.187 | -1.7545 | -1.43 | -1.5147 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8391
273 | 12 | -2.485 | -2.7261 | -2.107 | -2.8853 | -2.61 | -2.5624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.5383
274 | 13 | -2.996 | -3.2555 | -2.761 | -3.3784 | -3.26 | -3.1183 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.0027
275 | 14 | -3.234 | -3.3127 | -3.092 | -3.4483 | -3.42 | -3.2401 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.1209
276 | 15 | -3.202 | -2.9394 | -3.061 | -3.1098 | -3.14 | -2.9531 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.9337
277 | 16 | -2.922 | -2.2909 | -2.681 | -2.5271 | -2.61 | -2.3467 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.3867
278 | 17 | -2.521 | -1.6885 | -2.156 | -1.9379 | -2.01 | -1.8239 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8886
279 | 18 | -2.084 | -1.2498 | -1.647 | -1.4631 | -1.54 | -1.3771 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4086
280 | 19 | -1.63 | -0.8713 | -1.164 | -1.0152 | -1.09 | -0.93641 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.9444
281 | 20 | -1.128 | -0.45588 | -0.649 | -0.55242 | -0.58 | -0.46799 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4182
282 | 21 | -0.642 | -0.099993 | -0.157 | -0.17822 | -0.14 | -0.1179 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0306
283 | 22 | -0.314 | 0 | 0 | -0.0080085 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
284 | 23 | -0.097 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
285 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 680 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 1.186 | 0.99585 | 1.044 | 1.2516 | 1.17 | 1.2499 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.319
263 | 2 | 1.246 | 1.1111 | 1.154 | 1.3644 | 1.32 | 1.3728 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4032
264 | 3 | 1.341 | 1.1938 | 1.232 | 1.4425 | 1.42 | 1.4629 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4852
265 | 4 | 1.44 | 1.2656 | 1.301 | 1.5049 | 1.5 | 1.5405 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5523
266 | 5 | 1.514 | 1.2984 | 1.332 | 1.5323 | 1.55 | 1.5779 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5549
267 | 6 | 1.565 | 1.3219 | 1.366 | 1.5467 | 1.57 | 1.5974 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5877
268 | 7 | 1.591 | 1.3375 | 1.375 | 1.5469 | 1.59 | 1.609 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5839
269 | 8 | 1.327 | 1.0054 | 1.238 | 1.1609 | 1.3 | 1.0329 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9939
270 | 9 | 0.532 | 0.17368 | 0.416 | 0.15573 | 0.34 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
271 | 10 | 0 | -0.053007 | 0 | -0.11857 | -0.1 | -0.73104 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2939
272 | 11 | -0.759 | -1.9332 | -1.145 | -2.26 | -1.98 | -2.2417 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.334
273 | 12 | -2.604 | -4.069 | -2.926 | -4.3177 | -4.13 | -4.1403 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.8374
274 | 13 | -4.128 | -5.3127 | -4.197 | -5.523 | -5.48 | -5.2985 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.8444
275 | 14 | -4.575 | -5.5694 | -4.805 | -5.7122 | -5.85 | -5.4915 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.9385
276 | 15 | -4.445 | -5.054 | -4.909 | -5.0803 | -5.23 | -4.9288 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.6828
277 | 16 | -3.918 | -3.941 | -4.446 | -3.9171 | -4.14 | -3.8545 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.8771
278 | 17 | -2.906 | -2.3532 | -3.389 | -2.2347 | -2.55 | -2.2038 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.5774
279 | 18 | -1.436 | -0.51365 | -1.841 | -0.36295 | -0.61 | -0.27043 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.7869
280 | 19 | -0.295 | 0 | -0.479 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
281 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
282 | 21 | 0 | 0.064176 | 0 | 0.26604 | 0.2 | 0.39438 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
283 | 22 | 0 | 0.54736 | 0 | 0.76843 | 0.72 | 0.79929 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.6389
284 | 23 | 0.333 | 0.88344 | 0.516 | 1.0956 | 1.08 | 1.1242 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0626
285 | 24 | 0.92 | 1.0938 | 0.89 | 1.3198 | 1.29 | 1.3463 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2955
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 680 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.017 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
266 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
267 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
269 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
270 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
271 | 10 | -0.291 | -0.18419 | -0.168 | -0.32663 | -0.19 | -0.33152 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5687
272 | 11 | -0.988 | -1.0716 | -0.86 | -1.2062 | -0.99 | -1.094 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4224
273 | 12 | -1.632 | -1.9293 | -1.497 | -2.0156 | -1.84 | -1.892 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.0059
274 | 13 | -2.018 | -2.4066 | -2.001 | -2.5062 | -2.42 | -2.3763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.4004
275 | 14 | -2.189 | -2.4752 | -2.264 | -2.6048 | -2.61 | -2.493 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.4939
276 | 15 | -2.124 | -2.1675 | -2.242 | -2.348 | -2.42 | -2.2637 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.3018
277 | 16 | -1.896 | -1.6634 | -1.981 | -1.8957 | -2 | -1.8199 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8774
278 | 17 | -1.645 | -1.2613 | -1.642 | -1.505 | -1.59 | -1.4619 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.5159
279 | 18 | -1.403 | -0.97604 | -1.311 | -1.1869 | -1.27 | -1.1511 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1695
280 | 19 | -1.131 | -0.7202 | -1.003 | -0.87653 | -0.95 | -0.8396 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.8365
281 | 20 | -0.832 | -0.4781 | -0.694 | -0.57282 | -0.63 | -0.54058 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4822
282 | 21 | -0.555 | -0.27107 | -0.415 | -0.33075 | -0.37 | -0.30722 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2317
283 | 22 | -0.363 | -0.12549 | -0.215 | -0.16755 | -0.18 | -0.14209 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0751
284 | 23 | -0.224 | -0.025991 | -0.064 | -0.053704 | -0.05 | -0.022857 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
285 | 24 | -0.097 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 685 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 2.05 | 1.9212 | 2.033 | 2.1861 | 2.12 | 2.2164 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.2317
263 | 2 | 2.059 | 2.0146 | 2.096 | 2.2406 | 2.25 | 2.2966 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.268
264 | 3 | 2.139 | 2.0666 | 2.145 | 2.2855 | 2.32 | 2.3561 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.3285
265 | 4 | 2.243 | 2.1268 | 2.216 | 2.3336 | 2.39 | 2.4196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.3883
266 | 5 | 2.321 | 2.1569 | 2.249 | 2.3538 | 2.43 | 2.4442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.3751
267 | 6 | 2.373 | 2.1651 | 2.271 | 2.353 | 2.44 | 2.4533 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4092
268 | 7 | 2.401 | 2.1854 | 2.28 | 2.3559 | 2.46 | 2.4668 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4061
269 | 8 | 2.118 | 1.777 | 2.121 | 1.8836 | 2.09 | 1.7486 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7606
270 | 9 | 1.068 | 0.54801 | 1.204 | 0.46459 | 0.77 | 0.29652 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1732
271 | 10 | -0.479 | -0.95761 | -0.399 | -1.3367 | -1.11 | -1.3527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4394
272 | 11 | -1.956 | -2.8606 | -2.012 | -3.2585 | -3.12 | -3.1162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.8539
273 | 12 | -3.25 | -4.335 | -3.385 | -4.6823 | -4.62 | -4.5191 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.0859
274 | 13 | -4.289 | -5.2497 | -4.382 | -5.6082 | -5.6 | -5.4071 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.9249
275 | 14 | -4.731 | -5.3818 | -4.783 | -5.7135 | -5.83 | -5.4259 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.8207
276 | 15 | -4.545 | -4.6926 | -4.698 | -4.881 | -5.07 | -4.6952 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.4203
277 | 16 | -3.952 | -3.486 | -4.099 | -3.5937 | -3.87 | -3.5095 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.5118
278 | 17 | -2.904 | -1.8707 | -2.915 | -1.876 | -2.21 | -1.8248 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.1357
279 | 18 | -1.365 | -0.062132 | -1.224 | 0.036899 | -0.2 | 0.12836 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2244
280 | 19 | 0.009 | 1.0222 | 0.257 | 1.1009 | 1.07 | 1.0762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8852
281 | 20 | 0.767 | 1.6012 | 1.116 | 1.6905 | 1.71 | 1.6727 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5319
282 | 21 | 1.239 | 1.9179 | 1.645 | 2.0307 | 2.05 | 2.0601 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.9636
283 | 22 | 1.583 | 2.1437 | 1.993 | 2.2766 | 2.3 | 2.3472 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.2691
284 | 23 | 1.841 | 2.2881 | 2.203 | 2.4412 | 2.48 | 2.5334 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4257
285 | 24 | 2.007 | 2.3327 | 2.307 | 2.4984 | 2.54 | 2.6039 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.4875
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 685 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.449 | -0.049027 | 0 | -0.084479 | -0.04 | -0.052034 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0152
263 | 2 | -0.286 | 0.02692 | 0.078 | -0.025064 | 0.05 | 0.025254 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1171
264 | 3 | -0.155 | 0.11975 | 0.158 | 0.056452 | 0.13 | 0.145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2748
265 | 4 | -0.017 | 0.24941 | 0.244 | 0.17529 | 0.26 | 0.27949 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.3643
266 | 5 | 0.11 | 0.34005 | 0.332 | 0.27165 | 0.35 | 0.37362 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.4569
267 | 6 | 0.048 | 0.23558 | 0.247 | 0.16084 | 0.26 | 0.21087 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1508
268 | 7 | -0.274 | -0.1131 | -0.069 | -0.13512 | -0.09 | -0.099433 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2692
269 | 8 | -0.664 | -0.4792 | -0.457 | -0.53511 | -0.45 | -0.45575 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6689
270 | 9 | -1.032 | -0.89805 | -0.861 | -1.0194 | -0.91 | -0.92639 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1141
271 | 10 | -1.499 | -1.5518 | -1.365 | -1.7043 | -1.55 | -1.6327 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.7944
272 | 11 | -2.125 | -2.3959 | -1.979 | -2.5672 | -2.36 | -2.4664 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.5603
273 | 12 | -2.709 | -3.1327 | -2.56 | -3.316 | -3.14 | -3.1511 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.0351
274 | 13 | -3.08 | -3.4278 | -3.004 | -3.614 | -3.55 | -3.4891 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.3511
275 | 14 | -3.24 | -3.4049 | -3.231 | -3.6138 | -3.63 | -3.5104 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.3925
276 | 15 | -3.208 | -3.0702 | -3.192 | -3.3078 | -3.37 | -3.232 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.1967
277 | 16 | -3.006 | -2.5639 | -2.905 | -2.8517 | -2.95 | -2.7482 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.74
278 | 17 | -2.716 | -2.101 | -2.518 | -2.3954 | -2.49 | -2.3306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.3384
279 | 18 | -2.389 | -1.7475 | -2.126 | -1.9943 | -2.09 | -1.9487 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.9469
280 | 19 | -2.036 | -1.4176 | -1.731 | -1.5926 | -1.68 | -1.5442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.5536
281 | 20 | -1.631 | -1.0309 | -1.285 | -1.1479 | -1.19 | -1.089 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.091
282 | 21 | -1.237 | -0.69086 | -0.849 | -0.78159 | -0.76 | -0.75479 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.7646
283 | 22 | -0.974 | -0.49742 | -0.569 | -0.5735 | -0.51 | -0.54994 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5568
284 | 23 | -0.798 | -0.37088 | -0.383 | -0.43593 | -0.35 | -0.40268 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3834
285 | 24 | -0.634 | -0.25271 | -0.228 | -0.30738 | -0.23 | -0.26193 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.1929
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 695 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 1.225 | 1.145 | 1.202 | 1.384 | 1.31 | 1.3877 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4288
263 | 2 | 1.264 | 1.2047 | 1.253 | 1.4443 | 1.41 | 1.4641 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4731
264 | 3 | 1.356 | 1.2518 | 1.293 | 1.4903 | 1.48 | 1.5223 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5297
265 | 4 | 1.453 | 1.3012 | 1.34 | 1.5334 | 1.54 | 1.578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5807
266 | 5 | 1.526 | 1.3204 | 1.356 | 1.5491 | 1.57 | 1.6015 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.573
267 | 6 | 1.577 | 1.3355 | 1.381 | 1.5567 | 1.59 | 1.612 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5992
268 | 7 | 1.604 | 1.3459 | 1.385 | 1.5531 | 1.6 | 1.6183 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5913
269 | 8 | 1.34 | 1.0098 | 1.243 | 1.1644 | 1.31 | 1.0378 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9986
270 | 9 | 0.363 | 0.059474 | 0.42 | -0.078065 | 0.25 | -0.27649 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4912
271 | 10 | -1.088 | -1.666 | -1.046 | -2.0066 | -1.63 | -2.0859 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.0518
272 | 11 | -2.496 | -3.5885 | -2.585 | -3.9354 | -3.67 | -3.8622 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.4656
273 | 12 | -3.726 | -5.0849 | -3.941 | -5.3726 | -5.21 | -5.2547 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.7027
274 | 13 | -4.673 | -5.993 | -4.962 | -6.2586 | -6.22 | -6.1055 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -5.5447
275 | 14 | -5.066 | -6.0919 | -5.418 | -6.2995 | -6.42 | -6.1336 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -5.5477
276 | 15 | -4.931 | -5.5054 | -5.427 | -5.6031 | -5.73 | -5.4801 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -5.234
277 | 16 | -4.405 | -4.3565 | -4.905 | -4.3995 | -4.6 | -4.3483 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -4.392
278 | 17 | -3.392 | -2.7253 | -3.811 | -2.7038 | -3 | -2.6911 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.0628
279 | 18 | -1.92 | -0.87523 | -2.24 | -0.72678 | -1.02 | -0.72316 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2487
280 | 19 | -0.65 | 0.15843 | -0.863 | 0.31916 | 0.18 | 0.26566 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.1617
281 | 20 | 0.037 | 0.60708 | -0.003 | 0.74894 | 0.67 | 0.73538 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.5115
282 | 21 | 0.474 | 0.89914 | 0.556 | 1.0411 | 1 | 1.0332 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9408
283 | 22 | 0.783 | 1.1068 | 0.926 | 1.2788 | 1.24 | 1.2825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2618
284 | 23 | 1.011 | 1.2559 | 1.153 | 1.4531 | 1.42 | 1.4716 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4426
285 | 24 | 1.167 | 1.3349 | 1.283 | 1.5445 | 1.52 | 1.5777 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5352
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 695 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.422 | -0.13418 | -0.139 | -0.15693 | -0.14 | -0.13755 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0817
263 | 2 | -0.302 | -0.081538 | -0.074 | -0.10057 | -0.07 | -0.073529 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0092
264 | 3 | -0.209 | -0.026795 | -0.009 | -0.041091 | -0.02 | -0.00087619 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0929
265 | 4 | -0.115 | 0.034874 | 0.053 | 0.017247 | 0.04 | 0.071603 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1575
266 | 5 | -0.023 | 0.098044 | 0.115 | 0.071385 | 0.11 | 0.13714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2286
267 | 6 | -0.05 | 0.064405 | 0.057 | 0.032137 | 0.09 | 0.08276 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0287
268 | 7 | -0.242 | -0.089405 | -0.106 | -0.1231 | -0.06 | -0.096297 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2498
269 | 8 | -0.499 | -0.3116 | -0.331 | -0.38175 | -0.3 | -0.34347 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5429
270 | 9 | -0.773 | -0.61456 | -0.603 | -0.73521 | -0.63 | -0.68893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.8875
271 | 10 | -1.133 | -1.1481 | -0.989 | -1.2892 | -1.14 | -1.2695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4638
272 | 11 | -1.62 | -1.8678 | -1.499 | -2.0148 | -1.84 | -1.9765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.1122
273 | 12 | -2.108 | -2.5371 | -2.03 | -2.6747 | -2.53 | -2.6266 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.6031
274 | 13 | -2.48 | -2.9109 | -2.469 | -3.0711 | -3 | -3.0055 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.9348
275 | 14 | -2.649 | -2.9258 | -2.692 | -3.1133 | -3.12 | -3.0535 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.9919
276 | 15 | -2.582 | -2.5909 | -2.645 | -2.8203 | -2.88 | -2.7773 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.7708
277 | 16 | -2.354 | -2.0688 | -2.368 | -2.3445 | -2.44 | -2.3013 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.336
278 | 17 | -2.106 | -1.6542 | -2.019 | -1.947 | -2.02 | -1.9323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.9697
279 | 18 | -1.864 | -1.3655 | -1.681 | -1.6239 | -1.69 | -1.612 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.6179
280 | 19 | -1.593 | -1.1029 | -1.37 | -1.3044 | -1.36 | -1.2859 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2808
281 | 20 | -1.295 | -0.84841 | -1.058 | -0.98545 | -1.03 | -0.96142 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.9222
282 | 21 | -1.02 | -0.63671 | -0.778 | -0.73214 | -0.75 | -0.71544 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6746
283 | 22 | -0.83 | -0.49022 | -0.577 | -0.56394 | -0.55 | -0.55005 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.515
284 | 23 | -0.691 | -0.38407 | -0.425 | -0.44324 | -0.41 | -0.42662 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3792
285 | 24 | -0.562 | -0.28879 | -0.297 | -0.3341 | -0.31 | -0.31199 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2348
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 940 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
266 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
267 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
269 | 8 | 1.097 | 0.90177 | 2.4441 | 1.2639 | 1.13 | 1.2786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
270 | 9 | 1.669 | 1.1161 | 1.9321 | 1.5508 | 1.7 | 1.5794 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.0399
271 | 10 | 0.62 | 0.49385 | 1.2397 | 0.82256 | 0.91 | 0.84183 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9166
272 | 11 | 0.047 | 0.066615 | 0.51559 | 0.29741 | 0.44 | 0.30366 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1647
273 | 12 | 0 | 0 | 0 | 0 | 0.04 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
274 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
275 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
276 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
277 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
278 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
279 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
280 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
281 | 20 | 0 | 0 | 0 | 0 | 0 | 0.09175 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0497
282 | 21 | 0 | 0.086615 | 0.01799 | 0.12095 | 0.02 | 0.27159 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.3385
283 | 22 | 0.041 | 0.33452 | 0.26925 | 0.38542 | 0.25 | 0.52154 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.5907
284 | 23 | 0.243 | 0.54165 | 0.46845 | 0.61003 | 0.52 | 0.73879 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.7754
285 | 24 | 0.202 | 0 | 0 | 0 | 0.08 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 980 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
263 | 2 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
264 | 3 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
265 | 4 | #N/A | 0 | 0 | 0.010067 | 0 | 0.092844 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0032
266 | 5 | #N/A | 0 | 0 | 0.11176 | 0 | 0.21749 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1284
267 | 6 | 0.072 | 0 | 0 | 0.22968 | 0.1 | 0.32564 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2532
268 | 7 | 0.211 | 0 | 0.018134 | 0.32252 | 0.22 | 0.41999 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.3395
269 | 8 | 0.078 | 0 | 0.047822 | 0.19642 | 0.19 | 0.23403 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1423
270 | 9 | #N/A | 0 | 0 | 0 | 0.01 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
271 | 10 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
272 | 11 | #N/A | -0.028774 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
273 | 12 | -0.068 | -0.56154 | 0 | -0.11102 | -0.09 | -0.22351 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2953
274 | 13 | -0.668 | -1.192 | -0.5694 | -0.74762 | -0.69 | -0.73161 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.9751
275 | 14 | -1.302 | -1.5455 | -0.92744 | -1.1811 | -1.17 | -1.1455 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1313
276 | 15 | -1.555 | -1.6506 | -1.173 | -1.3476 | -1.35 | -1.2934 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2608
277 | 16 | -1.453 | -1.5424 | -1.2114 | -1.2768 | -1.35 | -1.2148 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1496
278 | 17 | -0.73 | -1.1511 | -1.0054 | -0.87926 | -1.05 | -0.8108 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.8191
279 | 18 | -0.092 | -0.46865 | -0.56114 | -0.21836 | -0.47 | -0.14797 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.1928
280 | 19 | #N/A | -0.10765 | -0.19504 | 0 | -0.05 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
281 | 20 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
282 | 21 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
283 | 22 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
284 | 23 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
285 | 24 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 980 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.241 | -0.18841 | -0.28999 | -0.21575 | -0.27 | -0.17298 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.1497
263 | 2 | -0.119 | -0.13027 | -0.22559 | -0.15588 | -0.21 | -0.10898 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0838
264 | 3 | -0.037 | -0.068221 | -0.15164 | -0.093652 | -0.14 | -0.038742 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
265 | 4 | 0 | -0.0086705 | -0.07752 | -0.024143 | -0.06 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
266 | 5 | 0 | 0 | -0.00322 | 0 | -0.01 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
267 | 6 | 0 | 0 | -0.03011 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
268 | 7 | 0 | -0.018269 | -0.10082 | -0.062989 | -0.06 | -0.023003 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0256
269 | 8 | -0.071 | -0.11586 | -0.18766 | -0.17091 | -0.16 | -0.1092 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.1744
270 | 9 | -0.236 | -0.24815 | -0.30235 | -0.30246 | -0.27 | -0.2488 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3505
271 | 10 | -0.487 | -0.50733 | -0.4882 | -0.52915 | -0.45 | -0.46854 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6653
272 | 11 | -0.832 | -0.86339 | -0.72195 | -0.82735 | -0.72 | -0.76822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.9954
273 | 12 | -1.184 | -1.1778 | -0.9537 | -1.0995 | -1 | -1.0533 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2254
274 | 13 | -1.422 | -1.3736 | -1.1675 | -1.3165 | -1.23 | -1.2706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4199
275 | 14 | -1.553 | -1.4517 | -1.3074 | -1.4417 | -1.39 | -1.3952 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.5019
276 | 15 | -1.593 | -1.3713 | -1.3421 | -1.438 | -1.42 | -1.39 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4628
277 | 16 | -1.517 | -1.1792 | -1.2783 | -1.33 | -1.34 | -1.2715 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.3051
278 | 17 | -1.417 | -1.0349 | -1.1854 | -1.2236 | -1.24 | -1.1727 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1872
279 | 18 | -1.284 | -0.93142 | -1.0758 | -1.1098 | -1.13 | -1.0609 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0497
280 | 19 | -1.121 | -0.81522 | -0.96104 | -0.96893 | -1 | -0.91946 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.9059
281 | 20 | -0.938 | -0.69185 | -0.82628 | -0.81412 | -0.86 | -0.76865 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.7371
282 | 21 | -0.788 | -0.58322 | -0.70182 | -0.68625 | -0.73 | -0.6432 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6113
283 | 22 | -0.638 | -0.49948 | -0.61213 | -0.59068 | -0.63 | -0.54605 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5265
284 | 23 | -0.512 | -0.42484 | -0.52449 | -0.5056 | -0.54 | -0.46032 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4338
285 | 24 | -0.387 | -0.33992 | -0.42934 | -0.41088 | -0.45 | -0.36221 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3246
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 985 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 1.202 | 0.9489 | 1.1713 | 1.1316 | 1.07 | 1.1818 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2859
263 | 2 | 1.224 | 1.0473 | 1.266 | 1.2332 | 1.2 | 1.2942 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.3787
264 | 3 | 1.323 | 1.1317 | 1.3543 | 1.3297 | 1.3 | 1.3966 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4837
265 | 4 | 1.408 | 1.2243 | 1.4513 | 1.4277 | 1.4 | 1.5015 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.583
266 | 5 | 1.439 | 1.2901 | 1.5133 | 1.5004 | 1.48 | 1.5771 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.6295
267 | 6 | 1.445 | 1.351 | 1.5837 | 1.5653 | 1.55 | 1.6428 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7082
268 | 7 | 1.459 | 1.4134 | 1.6344 | 1.6239 | 1.62 | 1.7074 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7534
269 | 8 | 1.294 | 1.226 | 1.6091 | 1.4296 | 1.52 | 1.4465 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5061
270 | 9 | 1.0285 | 0.63568 | 1.2523 | 0.87469 | 1.02 | 0.85185 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8278
271 | 10 | 0.106 | 0.19897 | 0.63558 | 0.34915 | 0.46 | 0.32364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1408
272 | 11 | -0.8215 | -0.34013 | -0.03353 | -0.25363 | -0.12 | -0.28825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5205
273 | 12 | -1.6695 | -0.98196 | -0.67357 | -0.93631 | -0.77 | -0.96318 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1878
274 | 13 | -2.3805 | -1.5878 | -1.2303 | -1.6478 | -1.48 | -1.6316 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.7328
275 | 14 | -2.566 | -1.9023 | -1.5163 | -2.0379 | -1.94 | -1.9744 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8033
276 | 15 | -2.464 | -1.9331 | -1.6801 | -2.082 | -2.02 | -2.0099 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.851
277 | 16 | -2.206 | -1.7333 | -1.6411 | -1.9005 | -1.94 | -1.8348 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.6621
278 | 17 | -1.521 | -1.2638 | -1.3568 | -1.3981 | -1.56 | -1.3251 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2508
279 | 18 | -0.817 | -0.54502 | -0.83413 | -0.63216 | -0.89 | -0.55512 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5355
280 | 19 | -0.11 | -0.13333 | -0.3958 | -0.18634 | -0.35 | -0.12032 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.1478
281 | 20 | 0.216 | 0.11696 | -0.11193 | 0.1006 | -0.04 | 0.17769 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.1325
282 | 21 | 0.499 | 0.34273 | 0.13546 | 0.33635 | 0.23 | 0.41925 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.3703
283 | 22 | 0.7242 | 0.54685 | 0.36388 | 0.5638 | 0.48 | 0.6443 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.6135
284 | 23 | 0.96 | 0.71216 | 0.55162 | 0.75784 | 0.71 | 0.84052 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.7935
285 | 24 | 1.158 | 0.82345 | 0.70288 | 0.89065 | 0.86 | 0.98099 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9337
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 985 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.821 | -0.64521 | -0.70663 | -0.71075 | -0.76 | -0.66171 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6566
263 | 2 | -0.701 | -0.55887 | -0.62235 | -0.62348 | -0.66 | -0.5713 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5613
264 | 3 | -0.574 | -0.46354 | -0.52812 | -0.52735 | -0.57 | -0.46544 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4336
265 | 4 | -0.483 | -0.3547 | -0.43146 | -0.42151 | -0.46 | -0.35659 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3378
266 | 5 | -0.4127 | -0.26008 | -0.33373 | -0.32772 | -0.35 | -0.25937 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2314
267 | 6 | -0.4064 | -0.25356 | -0.34526 | -0.33274 | -0.32 | -0.26648 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3252
268 | 7 | -0.5304 | -0.35224 | -0.43216 | -0.44088 | -0.4 | -0.38013 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4771
269 | 8 | -0.7226 | -0.49552 | -0.56288 | -0.59821 | -0.52 | -0.51857 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6473
270 | 9 | -0.9494 | -0.68807 | -0.73174 | -0.79838 | -0.68 | -0.71573 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.8628
271 | 10 | -1.2632 | -1.0367 | -0.97482 | -1.1091 | -0.94 | -1.0407 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2269
272 | 11 | -1.71 | -1.4712 | -1.2648 | -1.4971 | -1.29 | -1.4329 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.6172
273 | 12 | -2.024 | -1.8619 | -1.5421 | -1.8618 | -1.65 | -1.7925 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8717
274 | 13 | -2.243 | -2.0803 | -1.7885 | -2.1009 | -1.93 | -2.0441 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.0835
275 | 14 | -2.346 | -2.1666 | -1.9516 | -2.2354 | -2.11 | -2.1791 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.1765
276 | 15 | -2.342 | -2.0876 | -2.0008 | -2.2319 | -2.15 | -2.1762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.1543
277 | 16 | -2.25 | -1.8986 | -1.9428 | -2.1292 | -2.08 | -2.0485 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.9999
278 | 17 | -2.131 | -1.7366 | -1.8455 | -2.0064 | -1.98 | -1.9356 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8784
279 | 18 | -1.988 | -1.612 | -1.7221 | -1.8639 | -1.87 | -1.7994 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.7311
280 | 19 | -1.807 | -1.4718 | -1.5836 | -1.6925 | -1.72 | -1.6253 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.5729
281 | 20 | -1.61 | -1.3161 | -1.4224 | -1.5015 | -1.55 | -1.4325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.3833
282 | 21 | -1.433 | -1.1782 | -1.2731 | -1.3387 | -1.39 | -1.2707 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2429
283 | 22 | -1.281 | -1.0709 | -1.1615 | -1.2139 | -1.25 | -1.1431 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.138
284 | 23 | -1.15 | -0.97062 | -1.0547 | -1.0991 | -1.12 | -1.027 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0238
285 | 24 | -1.009 | -0.85843 | -0.93767 | -0.97318 | -1 | -0.89868 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.8843
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 995 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0.724 | 0.32105 | 0.40804 | 0.50876 | 0.42 | 0.53763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.5402
263 | 2 | 0.814 | 0.40368 | 0.48876 | 0.59729 | 0.54 | 0.62899 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.6264
264 | 3 | 0.942 | 0.47533 | 0.56563 | 0.67434 | 0.63 | 0.70796 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.722
265 | 4 | 1.054 | 0.55403 | 0.64603 | 0.74589 | 0.71 | 0.78477 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8112
266 | 5 | 1.142 | 0.60291 | 0.69388 | 0.78604 | 0.77 | 0.83089 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8516
267 | 6 | 1.221 | 0.64819 | 0.75613 | 0.81681 | 0.81 | 0.86691 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9206
268 | 7 | 1.285 | 0.68594 | 0.79633 | 0.8414 | 0.85 | 0.90136 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.9569
269 | 8 | 1.157 | 0.52924 | 0.76451 | 0.68673 | 0.76 | 0.69613 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.7132
270 | 9 | 0.53 | 0.086248 | 0.41712 | 0.24592 | 0.37 | 0.19219 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0537
271 | 10 | -0.675 | -0.50421 | -0.16807 | -0.3633 | -0.2 | -0.42045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6094
272 | 11 | -1.617 | -1.1965 | -0.79694 | -1.0539 | -0.88 | -1.1165 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2465
273 | 12 | -2.518 | -1.8905 | -1.3983 | -1.7987 | -1.6 | -1.8616 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8862
274 | 13 | -3.021 | -2.4977 | -1.9247 | -2.5159 | -2.34 | -2.5375 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.3996
275 | 14 | -3.186 | -2.7863 | -2.1968 | -2.8801 | -2.78 | -2.87 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.475
276 | 15 | -3.042 | -2.8206 | -2.3715 | -2.9303 | -2.83 | -2.9019 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.5327
277 | 16 | -2.718 | -2.6157 | -2.3468 | -2.7431 | -2.73 | -2.7176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.3569
278 | 17 | -2.122 | -2.1061 | -2.0834 | -2.2176 | -2.34 | -2.1893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.9634
279 | 18 | -1.32 | -1.3534 | -1.5865 | -1.4023 | -1.63 | -1.3747 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.2772
280 | 19 | -0.788 | -0.91496 | -1.1719 | -0.925 | -1.08 | -0.89967 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.9071
281 | 20 | -0.385 | -0.64822 | -0.90379 | -0.60955 | -0.75 | -0.57738 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6394
282 | 21 | -0.01 | -0.42283 | -0.6734 | -0.35944 | -0.48 | -0.32112 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4299
283 | 22 | 0.164 | -0.23074 | -0.46555 | -0.13628 | -0.25 | -0.10322 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.206
284 | 23 | 0.42 | -0.065507 | -0.2987 | 0.056384 | -0.04 | 0.091677 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.0414
285 | 24 | 0.618 | 0.055548 | -0.16436 | 0.19471 | 0.1 | 0.2338 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.0872
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 995 JUL 14
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.77 | -0.57478 | -0.6563 | -0.64079 | -0.68 | -0.61504 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5978
263 | 2 | -0.642 | -0.51269 | -0.5916 | -0.57552 | -0.61 | -0.54619 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.5257
264 | 3 | -0.541 | -0.44442 | -0.5172 | -0.5033 | -0.54 | -0.46646 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4303
265 | 4 | -0.434 | -0.36915 | -0.4428 | -0.42781 | -0.46 | -0.38577 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.357
266 | 5 | -0.328 | -0.29783 | -0.3681 | -0.35439 | -0.38 | -0.31121 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.2746
267 | 6 | -0.33 | -0.30657 | -0.3947 | -0.37247 | -0.37 | -0.32724 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.3681
268 | 7 | -0.462 | -0.38991 | -0.4652 | -0.46548 | -0.44 | -0.42475 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.4955
269 | 8 | -0.626 | -0.48515 | -0.5517 | -0.57861 | -0.54 | -0.53025 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6322
270 | 9 | -0.811 | -0.62671 | -0.6662 | -0.73081 | -0.66 | -0.68033 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.8054
271 | 10 | -1.077 | -0.92083 | -0.8518 | -0.98589 | -0.88 | -0.95144 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1186
272 | 11 | -1.447 | -1.2898 | -1.0853 | -1.3035 | -1.17 | -1.2752 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.442
273 | 12 | -1.687 | -1.6114 | -1.3168 | -1.5915 | -1.46 | -1.5789 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.6777
274 | 13 | -1.884 | -1.8125 | -1.5304 | -1.8176 | -1.71 | -1.8067 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.8698
275 | 14 | -1.984 | -1.888 | -1.6701 | -1.9425 | -1.86 | -1.9307 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.9514
276 | 15 | -1.971 | -1.8001 | -1.7047 | -1.9297 | -1.89 | -1.9149 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.906
277 | 16 | -1.872 | -1.5962 | -1.6406 | -1.8097 | -1.8 | -1.7802 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.7491
278 | 17 | -1.763 | -1.4401 | -1.5477 | -1.6975 | -1.69 | -1.6747 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.6324
279 | 18 | -1.643 | -1.3312 | -1.4379 | -1.5763 | -1.58 | -1.5534 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.4933
280 | 19 | -1.479 | -1.2069 | -1.3231 | -1.4243 | -1.44 | -1.3964 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.3478
281 | 20 | -1.294 | -1.0712 | -1.1882 | -1.2553 | -1.28 | -1.2236 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.1765
282 | 21 | -1.135 | -0.95683 | -1.0637 | -1.116 | -1.14 | -1.083 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.0536
283 | 22 | -1.041 | -0.87231 | -0.9739 | -1.0144 | -1.03 | -0.97738 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.9667
284 | 23 | -0.967 | -0.79533 | -0.8862 | -0.92336 | -0.93 | -0.88459 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.8723
285 | 24 | -0.881 | -0.70925 | -0.791 | -0.82306 | -0.84 | -0.78278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.758
| = | = | = | = | = | = | = | = | = | [8 empty] | =
CONDITIONED ZONE TEMPERATURES
CASE 640 FEB 1
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 12.7 | 11.1142 | 10 | 10.7291 | 10.63 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10
263 | 2 | 10.1 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10
264 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10
265 | 4 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10
266 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10
267 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10
268 | 7 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10
269 | 8 | 15 | 15.5 | 20 | 15.8147 | 15 | 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10
270 | 9 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
271 | 10 | 21.3 | 20.7841 | 20 | 21.32 | 21.16 | 21.7174 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.05
272 | 11 | 24.8 | 26.0342 | 26.64 | 26.4903 | 26.39 | 25.2174 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27
273 | 12 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27
274 | 13 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27
275 | 14 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27
276 | 15 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27
277 | 16 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27
278 | 17 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27
279 | 18 | 26.8 | 25.7064 | 27 | 25.4595 | 25.82 | 24.7749 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.44
280 | 19 | 25.4 | 21.3714 | 23.73 | 21.1465 | 21.21 | 21.2749 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20.92
281 | 20 | 22.8 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
282 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
283 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
284 | 23 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
285 | 24 | 16.8 | 12.9579 | 11.34 | 12.9018 | 13.55 | 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.31
| = | = | = | = | = | = | = | = | = | [8 empty] | =
CONDITIONED ZONE TEMPERATURES
CASE 940 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 18.1 | 16.6192 | 15.59 | 15.6174 | 16.04 | 14.9916 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.3
263 | 2 | 17.7 | 16.0221 | 15.02 | 15.0057 | 15.32 | 15.0095 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 14.67
264 | 3 | 17.2 | 15.4654 | 14.48 | 14.4319 | 14.71 | 13.9919 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 14.06
265 | 4 | 16.7 | 14.9003 | 13.9 | 13.8638 | 14.11 | 13.6703 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 13.46
266 | 5 | 16.3 | 14.3857 | 13.43 | 13.3569 | 13.55 | 12.9607 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 13.01
267 | 6 | 15.8 | 13.9037 | 12.92 | 12.884 | 13.05 | 12.5881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 12.48
268 | 7 | 15.4 | 13.4247 | 12.47 | 12.4205 | 12.53 | 12.0187 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 12.03
269 | 8 | 17.6 | 15.9016 | 20 | 15.9824 | 15.29 | 15.9576 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 12.43
270 | 9 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
271 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
272 | 11 | 20.7 | 20.1042 | 20 | 20 | 20.21 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
273 | 12 | 22.2 | 21.6771 | 20.54 | 20.9908 | 20.78 | 20.9881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.61
274 | 13 | 23.9 | 23.7146 | 22.49 | 23.1192 | 22.86 | 23.005 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 23.61
275 | 14 | 25.2 | 24.982 | 23.74 | 24.6214 | 24.53 | 24.4382 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.4
276 | 15 | 25.9 | 25.2873 | 24.64 | 25.2509 | 25.25 | 25.0064 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.99
277 | 16 | 25.8 | 25.2471 | 24.91 | 25.2715 | 25.47 | 24.9739 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.88
278 | 17 | 24.6 | 24.4059 | 24.35 | 24.483 | 24.94 | 24.1466 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24
279 | 18 | 23.2 | 22.6175 | 22.94 | 22.7901 | 23.5 | 22.4177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.09
280 | 19 | 22.2 | 21.3767 | 21.65 | 21.4689 | 22.04 | 21.0104 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20.82
281 | 20 | 21.4 | 20.564 | 20.76 | 20.5229 | 21.08 | 20.3503 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
282 | 21 | 20.8 | 20.0224 | 20 | 20.0026 | 20.23 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
283 | 22 | 20.2 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
284 | 23 | 19.6 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20
285 | 24 | 18.8 | 18.1003 | 18.01 | 18.0038 | 18.38 | 17.6553 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.39
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MAY 4
CASE 600 OR 900
HORIZONTAL SURFACE
(USE COLUMN B ONLY)
kWh | CODENAME: | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
0 | COUNTRY:
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
kWh |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
235 | 6 | 15 | 15.0006 | 15 | 21.25 | 17.81 | 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15
236 | 7 | 60 | 60.0025 | 60 | 64.75 | 60.75 | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60
237 | 8 | 111 | 111.0047 | 111 | 114.5833 | 110.5 | 111 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 111
238 | 9 | 158 | 158.0065 | 158 | 160.25 | 156.75 | 158 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 158
239 | 10 | 195 | 195.008 | 195 | 203.25 | 198.88 | 195 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 195
240 | 11 | 263 | 263.0108 | 263 | 259.8333 | 256.38 | 263 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 263
241 | 12 | 278 | 278.0116 | 278 | 276.5833 | 276 | 278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 278
242 | 13 | 277 | 277.0115 | 277 | 274.0833 | 274.88 | 277 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 277
243 | 14 | 259 | 259.0108 | 259 | 255.1667 | 257.25 | 259 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 259
244 | 15 | 227 | 227.0095 | 227 | 222 | 225.25 | 227 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 227
245 | 16 | 181 | 181.0076 | 181 | 172 | 177.12 | 181 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 181
246 | 17 | 104 | 104.0043 | 104 | 101.9167 | 107.25 | 104 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 104
247 | 18 | 53 | 53.0022 | 53 | 50.25 | 54.12 | 53 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 53
248 | 19 | 11 | 11.0004 | 11 | 10.5278 | 14.19 | 11 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLEAR DAY, JULY 14
CASE 600 OR 900
HORIZONTAL SURFACE
(USE COLUMN B ONLY)
kWh | CODENAME: | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
0 | COUNTRY:
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
kWh |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 1.4992 | 1.17 | 5.6503 | 2.88 | 1.8578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.8
235 | 6 | 90 | 82.0455 | 82.05 | 103.1926 | 90.78 | 89.6008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.43
236 | 7 | 275 | 264.1993 | 273.2 | 289.8646 | 272.39 | 275.5875 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 274.47
237 | 8 | 479 | 465.8199 | 477.91 | 493.4291 | 475.84 | 478.6209 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 478.01
238 | 9 | 668 | 656.5745 | 668 | 682.3352 | 666.65 | 669.4288 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 669.37
239 | 10 | 827 | 816.0523 | 827 | 837.8445 | 825.46 | 827.9708 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 828.38
240 | 11 | 941 | 931.7134 | 941 | 947.9972 | 939.78 | 941.9442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 942.66
241 | 12 | 1003 | 996.141 | 1003 | 1005.2373 | 1001.8 | 1004.1701 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1004.97
242 | 13 | 1008 | 1002.0363 | 1008 | 1004.0328 | 1005.59 | 1007.5518 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1008.22
243 | 14 | 955 | 951.5143 | 955 | 946.1468 | 952.44 | 954.4569 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 954.79
244 | 15 | 848 | 847.7872 | 848 | 835.4779 | 846.07 | 848.3258 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 848.14
245 | 16 | 696 | 697.2651 | 696 | 679.2595 | 693.34 | 695.7926 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 694.98
246 | 17 | 509 | 511.7801 | 509 | 489.9716 | 506.28 | 508.9129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 507.45
247 | 18 | 306 | 309.2767 | 304.41 | 285.8351 | 302.71 | 305.8694 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 303.92
248 | 19 | 114 | 116.1785 | 110.72 | 99.0838 | 112.8 | 113.5205 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 111.65
249 | 20 | 0 | 5.5971 | 3.65 | 4.4364 | 7.48 | 5.1513 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.02
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY SKY TEMPERATURE DATA
CASE 600 CLEAR/COLD FEB 1
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | -30.2822 | -22.8397 | -30.28 | -22.9659 | -30.02 | -24.4041 | -30.2822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -28.23
231 | 2 | -27.4567 | -26.6414 | -27.46 | -24.1358 | -27.59 | -28.908 | -27.4567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -25.06
232 | 3 | -33.8377 | -28.0897 | -33.84 | -25.3162 | -34.17 | -30.651 | -33.8377 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -32.9
233 | 4 | -37.567 | -33.7622 | -37.57 | -27.1947 | -37.85 | -35.7966 | -37.567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -37.3
234 | 5 | -35.0231 | -35.2444 | -35.02 | -26.8988 | -35.32 | -36.4345 | -35.0231 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -33.91
235 | 6 | -35.993 | -35.6508 | -35.99 | -26.6742 | -36.27 | -35.6524 | -35.993 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -34.83
236 | 7 | -38.7016 | -37.5801 | -38.7 | -27.3883 | -39.06 | -37.476 | -38.7016 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -38.4
237 | 8 | -35.4235 | -37.0009 | -35.42 | -26.6041 | -35.71 | -37.1982 | -35.4235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -34.25
238 | 9 | -36.8689 | -36.328 | -36.87 | -25.3596 | -37.21 | -36.2544 | -36.8689 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -36.56
239 | 10 | -36.1031 | -36.5645 | -36.1 | -24.4946 | -36.53 | -36.5874 | -36.1031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -35.9
240 | 11 | -34.5636 | -35.3739 | -34.56 | -23.1465 | -35.02 | -35.3983 | -34.5636 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -34.42
241 | 12 | -33.6763 | -34.1943 | -33.68 | -21.7912 | -34.15 | -34.1462 | -33.6763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -33.59
242 | 13 | -31.6698 | -32.6854 | -31.67 | -20.2132 | -32.27 | -32.6565 | -31.6698 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -31.77
243 | 14 | -33.2373 | -32.6302 | -33.24 | -20.6931 | -33.6 | -32.45 | -33.2373 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -33.37
244 | 15 | -33.224 | -33.3209 | -33.22 | -21.7664 | -33.59 | -33.132 | -33.224 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -33.42
245 | 16 | -33.5 | -33.4665 | -33.5 | -22.2074 | -33.87 | -33.233 | -33.5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -33.79
246 | 17 | -34.0382 | -33.8865 | -34.04 | -22.932 | -34.35 | -33.6218 | -34.0382 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -34.31
247 | 18 | -36.3464 | -35.3916 | -36.35 | -24.6208 | -36.61 | -35.0378 | -36.3464 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -36.64
248 | 19 | -36.4727 | -36.4941 | -36.47 | -25.9163 | -36.72 | -36.2502 | -36.4727 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -36.77
249 | 20 | -36.913 | -36.7865 | -36.91 | -26.5019 | -37.14 | -36.5459 | -36.913 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -37.18
250 | 21 | -37.9742 | -37.563 | -37.97 | -27.6142 | -38.24 | -37.3195 | -37.9742 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -38.24
251 | 22 | -38.9062 | -38.5529 | -38.91 | -28.9393 | -39.11 | -38.344 | -38.9062 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -39.09
252 | 23 | -38.9555 | -38.9993 | -38.96 | -29.4433 | -39.18 | -38.8709 | -38.9555 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -39.08
253 | 24 | -38.5188 | -38.7814 | -38.52 | -29.2659 | -38.79 | -38.7168 | -38.5188 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -38.58
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY SKY TEMPERATURE DATA
CASE 600 CLOUDY MAY 4
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 3.6876 | 0.38605 | 3.69 | -1.17 | 0.09 | 0.41396 | 3.6876 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.69
231 | 2 | 4.4245 | 0.40933 | 4.42 | -1.1879 | 0.67 | 0.36976 | 4.4245 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.43
232 | 3 | 3.8943 | 0.32324 | 3.89 | -1.261 | 0.04 | 0.3372 | 3.8943 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.9
233 | 4 | 3.6721 | 0.019551 | 3.67 | -1.4438 | -0.01 | -0.0004892 | 3.6721 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.68
234 | 5 | 3.6641 | -0.026626 | 3.66 | -1.4438 | -0.06 | -0.049894 | 3.6641 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.67
235 | 6 | 3.803 | -0.077933 | 3.8 | -1.4438 | -0.11 | -0.10199 | 3.803 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.81
236 | 7 | 4.3213 | 0.1937 | 4.32 | -1.1879 | 0.44 | 0.14095 | 4.3213 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.33
237 | 8 | 4.3945 | 0.43445 | 4.39 | -0.87772 | 0.44 | 0.41027 | 4.3945 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.4
238 | 9 | 4.9064 | 0.70848 | 4.91 | -0.53267 | 0.93 | 0.66268 | 4.9064 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.91
239 | 10 | 6.2008 | 1.807 | 6.2 | 0.6528 | 2.52 | 1.7115 | 6.2008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.21
240 | 11 | 6.9765 | 3.0787 | 6.98 | 1.865 | 3.53 | 3.0181 | 6.9765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.98
241 | 12 | 6.2647 | 3.2866 | 6.26 | 2.0953 | 3.08 | 3.3069 | 6.2647 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.27
242 | 13 | 4.1911 | 2.1422 | 4.19 | 0.88422 | 1.37 | 2.2335 | 4.1911 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.19
243 | 14 | 3.1788 | 0.78812 | 3.18 | -0.55214 | 0.32 | 0.85375 | 3.1788 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.17
244 | 15 | 1.9243 | -0.62158 | 1.92 | -2.0361 | -1.39 | -0.51745 | 1.9243 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.91
245 | 16 | 1.1489 | -0.73525 | 1.15 | -1.9974 | -0.21 | -0.76901 | 1.1489 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.12
246 | 17 | 3.2979 | -0.44746 | 3.3 | -1.8299 | -0.63 | -0.39529 | 3.2979 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.29
247 | 18 | 3.2977 | -0.64839 | 3.3 | -2.1057 | -0.64 | -0.6146 | 3.2977 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.29
248 | 19 | 2.4978 | -0.91461 | 2.5 | -2.3646 | -1.12 | -0.85587 | 2.4978 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.49
249 | 20 | 1.9983 | -1.4056 | 2 | -2.9405 | -1.62 | -1.3469 | 1.9983 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.99
250 | 21 | 2.0062 | -1.607 | 2.01 | -3.2197 | -1.57 | -1.5768 | 2.0062 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2
251 | 22 | 1.8319 | -1.9502 | 1.83 | -3.7455 | -2.24 | -1.8894 | 1.8319 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.83
252 | 23 | 0.95143 | -2.8551 | 0.95 | -4.7857 | -3.35 | -2.7778 | 0.95143 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.95
253 | 24 | 0.95172 | -3.3493 | 0.95 | -5.2605 | -3.34 | -3.3333 | 0.95172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.95
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY SKY TEMPERATURE DATA
CASE 600 CLEAR/HOT JULY 14
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0.75693 | 0.90277 | 0.76 | 4.3575 | 0.7 | 1.0389 | 0.75693 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.74
231 | 2 | 0.16261 | 0.31055 | 0.163 | 3.8578 | 0.1 | 0.40274 | 0.16261 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.21
232 | 3 | -1.4341 | -0.83045 | -1.43 | 2.9526 | -1.36 | -0.72718 | -1.4341 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.18
233 | 4 | -2.7015 | -2.2461 | -2.7 | 1.8114 | -2.64 | -2.1863 | -2.7015 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -2.41
234 | 5 | -4.1002 | -3.5856 | -4.1 | 0.74467 | -4.05 | -3.5387 | -4.1002 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -3.77
235 | 6 | -1.779 | -2.9391 | -1.78 | 1.7866 | -1.82 | -3.0874 | -1.779 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -1.53
236 | 7 | 0.21141 | -0.80157 | 0.21 | 4.4173 | 0.27 | -0.93306 | 0.21141 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.58
237 | 8 | 1.1998 | 0.63558 | 1.2 | 6.596 | 1.19 | 0.56357 | 1.1998 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.48
238 | 9 | 2.2849 | 1.6749 | 2.28 | 8.3915 | 2.34 | 1.6181 | 2.2849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.59
239 | 10 | 5.0591 | 3.6938 | 5.06 | 10.7117 | 5.18 | 3.5737 | 5.0591 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.38
240 | 11 | 5.4079 | 5.1376 | 5.41 | 12.6113 | 5.23 | 5.1703 | 5.4079 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.35
241 | 12 | 5.1147 | 5.1381 | 5.11 | 13.2726 | 5.13 | 5.2388 | 5.1147 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.17
242 | 13 | 5.5711 | 5.2613 | 5.57 | 13.895 | 5.64 | 5.3636 | 5.5711 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.59
243 | 14 | 4.9914 | 5.1527 | 4.99 | 14.3919 | 4.83 | 5.3363 | 4.9914 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.69
244 | 15 | 6.0132 | 5.4585 | 6.01 | 14.9 | 6.27 | 5.6052 | 6.0132 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.06
245 | 16 | 5.4557 | 5.6185 | 5.46 | 14.7769 | 5.29 | 5.8681 | 5.4557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.02
246 | 17 | 6.5386 | 5.9695 | 6.54 | 14.4692 | 6.77 | 6.1476 | 6.5386 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.46
247 | 18 | 5.6681 | 5.9794 | 5.67 | 13.5976 | 5.56 | 6.2678 | 5.6681 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.23
248 | 19 | 5.1895 | 5.3256 | 5.19 | 12.3123 | 5.12 | 5.5904 | 5.1895 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.8
249 | 20 | 5.7177 | 5.4067 | 5.72 | 11.5045 | 5.75 | 5.6202 | 5.7177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.07
250 | 21 | 2.1391 | 3.6698 | 2.14 | 9.4472 | 2.22 | 4.052 | 2.1391 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.96
251 | 22 | 2.1388 | 2.0509 | 2.14 | 7.9167 | 2.07 | 2.235 | 2.1388 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.87
252 | 23 | 1.541 | 1.7227 | 1.54 | 7.1679 | 1.56 | 1.9 | 1.541 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.44
253 | 24 | 0.44827 | 0.85954 | 0.45 | 5.9239 | 0.53 | 1.015 | 0.44827 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.49
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/COLD DAY, FEB 1
CASE 600
SOUTH WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
235 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
236 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
237 | 8 | 104.3 | 82.0324 | 62.99 | 109.5631 | 98.09 | 106.3916 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 102.66
238 | 9 | 325.7 | 297.541 | 321.42 | 323.8 | 305.31 | 323.2919 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 317.8
239 | 10 | 484.4 | 459.7525 | 491.87 | 484.0809 | 471.51 | 482.6422 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 474.36
240 | 11 | 593.5 | 578.5582 | 608.92 | 591.9351 | 588.43 | 593.3244 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 584.18
241 | 12 | 653.9 | 652.8082 | 673.56 | 648.7354 | 646.8 | 655.1426 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 645.24
242 | 13 | 665 | 673.3877 | 684.62 | 654.8384 | 656.6 | 665.9038 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 656.08
243 | 14 | 623.5 | 628.6623 | 641 | 609.2696 | 617.5 | 624.0771 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 614.43
244 | 15 | 534.1 | 528.0285 | 543.97 | 513.0433 | 523.9 | 531.1272 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 523.63
245 | 16 | 396.8 | 378.3411 | 395.66 | 366.6641 | 378.6 | 392.8611 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 386.38
246 | 17 | 210.3 | 191.9413 | 184.45 | 178.3747 | 190.97 | 204.1309 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 202.53
247 | 18 | 0 | 14.3991 | 4.82 | 9.7889 | 10.84 | 18.3687 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.86
248 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/COLD DAY, FEB 1
CASE 660
SOUTH LOW-E WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
235 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
236 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
237 | 8 | 55.73 | 50.937 | 41.95 | 58.7036 | 52.46 | 56.996 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 55.83
238 | 9 | 176.5 | 180.8792 | 200.8 | 175.1923 | 165.67 | 175.7302 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 174.62
239 | 10 | 265.7 | 278.4931 | 297.08 | 263.0242 | 257.88 | 264.7322 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 262.34
240 | 11 | 327.31 | 348.905 | 362.95 | 322.5677 | 323.46 | 326.2696 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 324.52
241 | 12 | 361.31 | 391.0585 | 399.66 | 354.5078 | 356.29 | 360.9121 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 359.54
242 | 13 | 367.54 | 404.3853 | 405.96 | 357.9765 | 361.81 | 367.0186 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 365.78
243 | 14 | 344.22 | 377.3723 | 381.03 | 332.2657 | 339.8 | 343.5482 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 341.84
244 | 15 | 293.82 | 316.992 | 326.05 | 278.943 | 287.23 | 291.6286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 290.15
245 | 16 | 216.33 | 229.4327 | 242.52 | 198.6673 | 206.18 | 214.6368 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 212.98
246 | 17 | 112.91 | 117.7938 | 119.32 | 95.7857 | 102.75 | 109.8074 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 110.56
247 | 18 | 0 | 9.06 | 3.3 | 5.1964 | 5.76 | 9.7258 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.65
248 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/COLD DAY, FEB 1
CASE 670
SOUTH SINGLE-PANE WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
235 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
236 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
237 | 8 | 138.85 | 107.13 | 81.98 | 144.9621 | 130.57 | 140.083 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 138.34
238 | 9 | 409.45 | 362.8681 | 394.31 | 408.8652 | 385.67 | 406.3398 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 404.72
239 | 10 | 592.98 | 545.2226 | 584.9 | 596.1031 | 580.1 | 591.3496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 588.22
240 | 11 | 719.04 | 675.1871 | 714.8 | 720.937 | 713.01 | 718.8377 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 715.67
241 | 12 | 788.87 | 749.7897 | 786.82 | 786.606 | 781.74 | 789.0166 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 785.88
242 | 13 | 801.72 | 768.3238 | 799.14 | 793.6699 | 793.35 | 801.25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 798.34
243 | 14 | 753.75 | 720.0014 | 750.28 | 740.9315 | 747 | 753.2139 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 750.45
244 | 15 | 650.33 | 613.0512 | 642.14 | 629.5384 | 639.47 | 647.3005 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 645.43
245 | 16 | 492.04 | 452.897 | 477 | 459.3639 | 472.35 | 486.7755 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 485.29
246 | 17 | 272.44 | 241.2176 | 233.64 | 233.5125 | 248.72 | 265.4371 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 266.37
247 | 18 | 0 | 19.1922 | 6.44 | 13.5578 | 14.74 | 24.9891 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.99
248 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLOUDY DAY, MAY 4
CASE 600
SOUTH WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
235 | 6 | 5.6 | 5.76 | 5.49 | 6.5505 | 5.81 | 4.6924 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.52
236 | 7 | 21.85 | 23.0255 | 21.96 | 20.1724 | 19.89 | 19.0292 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.28
237 | 8 | 39.76 | 42.4983 | 40.63 | 35.7642 | 36.03 | 35.3106 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 33.58
238 | 9 | 56.42 | 60.5559 | 57.83 | 50.3329 | 51.69 | 50.5672 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 48.4
239 | 10 | 69.73 | 74.7815 | 71.37 | 64.481 | 66.46 | 63.0453 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60.55
240 | 11 | 94.02 | 100.3258 | 96.26 | 83.2627 | 86.72 | 85.9692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 82.73
241 | 12 | 99.56 | 105.248 | 101.75 | 89.1256 | 94 | 91.4367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.06
242 | 13 | 99.19 | 104.1118 | 101.39 | 88.2229 | 93.56 | 91.0569 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 87.69
243 | 14 | 92.55 | 97.1633 | 94.8 | 81.5371 | 86.87 | 84.5365 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 81.33
244 | 15 | 80.82 | 85.3291 | 83.09 | 70.1431 | 75.05 | 73.2554 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 70.32
245 | 16 | 64.17 | 68.2121 | 66.25 | 53.6776 | 58.03 | 57.6238 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 55.07
246 | 17 | 37.29 | 39.5371 | 38.07 | 31.766 | 34.87 | 33.0767 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 31.4
247 | 18 | 19.35 | 20.2628 | 19.4 | 15.6051 | 17.73 | 16.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.17
248 | 19 | 4.09 | 4.2104 | 4.03 | 3.2381 | 4.62 | 3.4323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.3
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLOUDY DAY, MAY 4
CASE 660
SOUTH LOW-E WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
235 | 6 | 3.06 | 3.544 | 3.54 | 3.5641 | 3.16 | 2.5704 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.51
236 | 7 | 11.96 | 14.1619 | 14.16 | 10.9757 | 10.83 | 10.4236 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10.14
237 | 8 | 21.77 | 26.0993 | 26.2 | 19.4591 | 19.62 | 19.3421 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.62
238 | 9 | 30.88 | 37.2213 | 37.3 | 27.3858 | 28.16 | 27.6992 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 26.84
239 | 10 | 38.17 | 46.0006 | 46.03 | 35.0837 | 36.2 | 34.5344 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 33.57
240 | 11 | 51.47 | 61.4812 | 62.09 | 45.3028 | 47.23 | 47.0914 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.87
241 | 12 | 54.5 | 64.2908 | 65.63 | 48.4927 | 51.2 | 50.0863 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 48.83
242 | 13 | 54.3 | 63.1249 | 65.39 | 48.0015 | 50.96 | 49.8783 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 48.62
243 | 14 | 50.67 | 58.8997 | 61.14 | 44.3638 | 47.31 | 46.3066 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.09
244 | 15 | 44.24 | 51.7282 | 53.59 | 38.1645 | 40.88 | 40.1271 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 38.99
245 | 16 | 35.13 | 41.4256 | 42.73 | 29.2057 | 31.61 | 31.5646 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30.53
246 | 17 | 20.41 | 24.1701 | 24.55 | 17.2837 | 18.99 | 18.1185 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.41
247 | 18 | 10.59 | 12.4348 | 12.51 | 8.4907 | 9.66 | 9.193 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 8.97
248 | 19 | 2.24 | 2.5852 | 2.6 | 1.7618 | 2.52 | 1.8801 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.83
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLOUDY DAY, MAY 4
CASE 670
SOUTH SINGLE-PANE WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
235 | 6 | 7.01 | 6.9223 | 6.93 | 8.271 | 7.24 | 5.8743 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.87
236 | 7 | 27.38 | 27.6826 | 27.74 | 25.471 | 24.8 | 23.8222 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 23.73
237 | 8 | 49.82 | 51.1502 | 51.32 | 45.1581 | 44.92 | 44.2044 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 43.59
238 | 9 | 70.69 | 72.8793 | 73.05 | 63.5536 | 64.45 | 63.3037 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 62.83
239 | 10 | 87.37 | 90.0133 | 90.15 | 81.4178 | 82.87 | 78.9248 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 78.6
240 | 11 | 117.8 | 121.0763 | 121.59 | 105.1329 | 108.12 | 107.6225 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 107.39
241 | 12 | 124.74 | 127.4075 | 128.53 | 112.5357 | 117.2 | 114.4671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 114.31
242 | 13 | 124.27 | 126.1131 | 128.06 | 111.3958 | 116.65 | 113.9917 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 113.83
243 | 14 | 115.96 | 117.7605 | 119.74 | 102.9539 | 108.31 | 105.829 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 105.58
244 | 15 | 101.26 | 103.3009 | 104.95 | 88.5672 | 93.57 | 91.7065 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 91.28
245 | 16 | 80.4 | 82.5129 | 83.68 | 67.7768 | 72.35 | 72.1377 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 71.48
246 | 17 | 46.72 | 47.709 | 48.08 | 40.1098 | 43.48 | 41.4079 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 40.77
247 | 18 | 24.25 | 24.4004 | 24.5 | 19.704 | 22.11 | 21.0096 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21
248 | 19 | 5.13 | 5.0665 | 5.09 | 4.0886 | 5.76 | 4.2968 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.29
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/HOT DAY, JUL 14
CASE 600
SOUTH WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0.34752 | 0.43 | 1.6849 | 0.8 | 0.66207 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.63
235 | 6 | 15.55 | 9.793 | 12.51 | 16.1367 | 15.28 | 15.6873 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 14.73
236 | 7 | 31.61 | 21.8537 | 28.06 | 33.0345 | 32.92 | 32.4711 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30.77
237 | 8 | 47.98 | 35.0242 | 44.78 | 48.9027 | 49.71 | 48.7734 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 46.4
238 | 9 | 66.84 | 52.8909 | 64.53 | 70.5019 | 72.36 | 71.7945 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 65.59
239 | 10 | 112.79 | 106.0912 | 113.53 | 116.644 | 117.05 | 118.4204 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 109.77
240 | 11 | 166.86 | 171.3254 | 172.34 | 169.4457 | 169.35 | 170.3654 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 163.45
241 | 12 | 201.93 | 214.7217 | 211.22 | 201.8158 | 204.8 | 209.7239 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 198.86
242 | 13 | 204.75 | 213.836 | 214.69 | 201.2382 | 207.38 | 210.9664 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 201.2
243 | 14 | 173.86 | 181.0836 | 181.43 | 168.1713 | 176.25 | 180.3064 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 169.91
244 | 15 | 121.01 | 121.3543 | 124.33 | 115.2723 | 125.09 | 127.6724 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 117.42
245 | 16 | 72.45 | 63.7931 | 70.83 | 69.6148 | 77.7 | 75.3431 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 70.22
246 | 17 | 50.43 | 37.6588 | 47.22 | 48.6162 | 52.17 | 51.0656 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 48.58
247 | 18 | 34.69 | 24.2426 | 30.56 | 32.6887 | 35.49 | 34.9664 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 33.2
248 | 19 | 18.13 | 11.6997 | 14.58 | 15.6631 | 17.72 | 18.0325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.98
249 | 20 | 0 | 1.1413 | 1.22 | 1.4014 | 2.08 | 1.895 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.76
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/HOT DAY, JUL 14
CASE 660
SOUTH LOW-E WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0.21439 | 0.28 | 0.91674 | 0.44 | 0.36266 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.35
235 | 6 | 8.51 | 6.0253 | 8.07 | 8.7799 | 8.33 | 8.593 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 8.16
236 | 7 | 17.3 | 13.4169 | 18.1 | 17.9739 | 17.93 | 17.7867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.06
237 | 8 | 26.27 | 21.4445 | 28.88 | 26.6079 | 27.07 | 26.7166 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 25.73
238 | 9 | 36.47 | 32.3826 | 43.25 | 38.6289 | 39.24 | 39.1157 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.83
239 | 10 | 60.56 | 66.3123 | 82.86 | 63.0283 | 62.79 | 63.6391 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60.89
240 | 11 | 88.94 | 107.1366 | 124.7 | 90.4757 | 90.23 | 90.5877 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 89.22
241 | 12 | 107.5 | 133.6999 | 149.98 | 107.4787 | 108.79 | 111.2626 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 108.09
242 | 13 | 109.01 | 132.4799 | 152.17 | 107.1723 | 110.14 | 111.9095 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 109.34
243 | 14 | 92.64 | 112.4723 | 130.74 | 89.8075 | 93.84 | 95.7693 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 92.65
244 | 15 | 64.87 | 75.3683 | 90.97 | 62.3178 | 67.02 | 68.4197 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 64.93
245 | 16 | 39.45 | 38.9794 | 48.68 | 38.1416 | 42.07 | 41.0134 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 39.48
246 | 17 | 27.6 | 22.8693 | 30.45 | 26.4518 | 28.42 | 27.9722 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 26.94
247 | 18 | 18.99 | 14.709 | 19.71 | 17.7857 | 19.33 | 19.1536 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.41
248 | 19 | 9.92 | 7.1153 | 9.4 | 8.5222 | 9.65 | 9.8777 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.42
249 | 20 | 0 | 0.69581 | 0.79 | 0.76247 | 1.13 | 1.038 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.98
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/HOT DAY, JUL 14
CASE 670
SOUTH SINGLE-PANE WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
234 | 5 | 0 | 0.41726 | 0.54 | 2.1275 | 1 | 0.82883 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.82
235 | 6 | 19.48 | 11.7918 | 15.8 | 20.3752 | 19.06 | 19.6385 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19.12
236 | 7 | 39.61 | 26.3554 | 35.45 | 41.7114 | 41.04 | 40.6497 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 39.94
237 | 8 | 60.11 | 42.3184 | 56.56 | 61.7496 | 61.97 | 61.0581 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60.24
238 | 9 | 89.08 | 67.7615 | 86.7 | 96.4962 | 94.38 | 95.0519 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 91.76
239 | 10 | 163.22 | 144.8439 | 164.26 | 170.6848 | 166.3 | 171.5706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 168.67
240 | 11 | 238.46 | 229.0314 | 244.33 | 244.3135 | 238.75 | 245.2683 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 245.12
241 | 12 | 283.59 | 280.7528 | 293.03 | 286.2069 | 284.99 | 294.3631 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 290.49
242 | 13 | 287.12 | 281.1221 | 297.25 | 285.4691 | 288.31 | 296.2153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 293.36
243 | 14 | 247.65 | 242.0489 | 255.91 | 242.6571 | 247.87 | 257.3993 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 253.65
244 | 15 | 175.19 | 166.4995 | 179.73 | 168.6678 | 178.35 | 185.0807 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 180.39
245 | 16 | 98.49 | 83.7436 | 97.78 | 94.9682 | 103.01 | 100.6228 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 100.66
246 | 17 | 63.18 | 45.4814 | 59.64 | 61.3859 | 65.1 | 63.9276 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 63.06
247 | 18 | 43.46 | 29.321 | 38.6 | 41.2749 | 44.25 | 43.7735 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 43.1
248 | 19 | 22.72 | 14.1359 | 18.42 | 19.7772 | 22.1 | 22.5744 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.04
249 | 20 | 0 | 1.3866 | 1.54 | 1.7694 | 2.6 | 2.3722 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.29
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| = | = | = | = | = | = | = | = | = | [8 empty] | =
CONVECTIVE HEAT TRANSFER COEFFICIENT DATA
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Exterior, Annual Average
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
0 | Window | [17 empty] | Case 670
0 | HC Wall
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 200 (εext=0.1; εint=0.1; αext=0.1; high cond. wall element)
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Exterior, Annual Hourly Maximum
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Exterior, Annual Hourly Minimum
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Interior, Annual Average
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
0 | Window | [17 empty] | Case 670
0 | HC Wall
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 200 (εext=0.1; εint=0.1; αext=0.1; high cond. wall element)
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Interior, Annual Hourly Maximum
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Interior, Annual Hourly Minimum
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall

## BSIMAC
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracking colors are:
Red is for edits from June 2013 through April 2018 distribution for the Round 3 sim trial draft.
| Software: | BSIMAC | BSIMAC 9
| Version: |  | 9.0.74
| Date of Results: |  | 2019-05-25
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.05 | 5.822 | 3.255 | Nov | 26 | 8 | 5.65 | Jan | 22 | 15
| 610 | 4.163 | 4.299 | 3.166 | Nov | 26 | 8 | 5.466 | Jan | 22 | 15
| 620 | 4.37 | 4.404 | 3.145 | Dec | 31 | 24 | 4.704 | Jun | 26 | 18
| 630 | 4.923 | 3.074 | 3.252 | Dec | 31 | 24 | 4.121 | Jun | 26 | 18
| 640 | 2.682 | 5.804 | 4.633 | Feb | 8 | 9 | 5.65 | Jan | 22 | 15
| 650 | 0 | 4.629 | 0 |  |  |  | 5.648 | Jan | 22 | 15
| 660 | 3.574 | 3.014 | 2.62 | Nov | 26 | 8 | 3.343 | Oct | 18 | 15
| 670 | 5.484 | 6.539 | 4.122 | Nov | 26 | 8 | 6.217 | Oct | 18 | 14
| 680 | 2.219 | 5.938 | 2.126 | Nov | 26 | 8 | 5.761 | Jan | 22 | 15
| 685 | 4.532 | 9.13 | 3.169 | Nov | 26 | 8 | 6.318 | Jan | 22 | 15
| 695 | 2.709 | 8.755 | 2.138 | Nov | 26 | 8 | 6.232 | Jan | 22 | 15
| 900 | 1.726 | 2.714 | 2.551 | Feb | 8 | 24 | 3.039 | Oct | 1 | 15
| 910 | 2.163 | 1.484 | 2.761 | Feb | 8 | 24 | 2.493 | Oct | 18 | 14
| 920 | 3.5 | 3.128 | 2.895 | Nov | 26 | 8 | 3.481 | Jun | 26 | 18
| 930 | 4.27 | 2.161 | 2.968 | Dec | 31 | 24 | 3.052 | Jun | 26 | 18
| 940 | 1.389 | 2.613 | 3.882 | Feb | 8 | 9 | 3.158 | Oct | 1 | 15
| 950 | 0 | 0.586 | 0 |  |  |  | 2.366 | Sep | 10 | 15
960
| 980 | 0.72 | 3.501 | 1.693 | Feb | 8 | 24 | 3.384 | Oct | 18 | 14
| 985 | 2.801 | 7.273 | 2.754 | Feb | 8 | 24 | 3.977 | Oct | 18 | 14
| 995 | 1.33 | 7.482 | 1.711 | Nov | 26 | 8 | 4.129 | Jan | 22 | 14
| 195 | 4.217 | 0.712 | 1.802 | Dec | 31 | 24 | 1.118 | Jun | 26 | 17
| 200 | 5.041 | 0.839 | 2.272 | Nov | 26 | 8 | 1.271 | Jun | 26 | 17
| 210 | 5.627 | 0.688 | 2.374 | Dec | 31 | 24 | 1.193 | Jun | 26 | 17
| 215 | 5.652 | 0.952 | 2.521 | Nov | 26 | 8 | 1.393 | Jun | 26 | 17
| 220 | 6.377 | 0.803 | 2.631 | Nov | 26 | 8 | 1.336 | Jun | 26 | 18
| 230 | 9.851 | 1.184 | 4.219 | Dec | 31 | 24 | 1.994 | Jun | 26 | 17
| 240 | 5.116 | 1.287 | 2.431 | Nov | 26 | 8 | 1.534 | Jun | 26 | 18
| 250 | 4.733 | 3.612 | 2.631 | Nov | 26 | 8 | 2.913 | Sep | 12 | 14
270
280
290
300
310
320
| 395 | 4.565 | 0.021 | 1.948 | Dec | 31 | 24 | 0.547 | Jun | 26 | 18
| 400 | 5.906 | 0.063 | 2.559 | Nov | 26 | 8 | 0.798 | Jun | 26 | 18
| 410 | 7.63 | 0.096 | 3.338 | Dec | 31 | 24 | 1.011 | Jun | 26 | 17
| 420 | 6.399 | 0.228 | 3.138 | Dec | 31 | 24 | 1.208 | Jun | 26 | 17
| 430 | 5.171 | 1.084 | 3.3 | Dec | 31 | 24 | 2.167 | Jun | 26 | 16
440
| 450 | 3.743 | 6.172 | 2.989 | Nov | 26 | 8 | 5.812 | Jan | 22 | 15
| 460 | 3.828 | 6.26 | 3.055 | Nov | 26 | 8 | 5.804 | Jan | 22 | 15
| 470 | 4.042 | 5.987 | 3.118 | Nov | 26 | 8 | 5.695 | Jan | 22 | 15
| 800 | 5.141 | 0.473 | 2.957 | Dec | 31 | 24 | 1.286 | Jun | 26 | 16
810
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 26.1 | -9.9 | Nov | 26 | 8 | 63.4 | Oct | 18 | 17
| 900FF | 25.5 | 0.6 | Feb | 8 | 11 | 46 | Oct | 1 | 17
| 650FF | 17.6 | -16.7 | Dec | 31 | 24 | 62.1 | Oct | 18 | 17
| 950FF | 15 | -13.2 | Dec | 31 | 24 | 37.1 | Oct | 1 | 17
| 680FF | 31.8 | -5.7 | Feb | 8 | 11 | 72.5 | Jan | 22 | 17
| 980FF | 30.7 | 7.3 | Feb | 8 | 11 | 49.7 | Oct | 1 | 17
960
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1670
| NORTH | 453
| EAST | 1061
| SOUTH | 1387
| WEST | 997
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 820
| 660/South | 447
| 670/South | 1037
| 620/West | 598
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 641
| 630/West | 438
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
600
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 663.99 | 475.4 | 3.1 | 29 | 7 | 5.65 | 22 | 15 | 277.8 | 73.3141 | 2.322 | 7 | 7 | 1.982 | 22 | 16
| Feb | 653.26 | 349.2 | 3.041 | 9 | 7 | 4.9211 | 15 | 15 | 307.4 | 24.0087 | 2.551 | 8 | 24 | 1.096 | 15 | 16
| Mar | 433.508 | 450.3 | 2.275 | 2 | 7 | 4.4579 | 24 | 14 | 134.4 | 86.3882 | 1.774 | 16 | 7 | 1.508 | 10 | 15
| Apr | 511.036 | 218.7 | 2.446 | 3 | 6 | 3.4735 | 12 | 14 | 275.7 | 29.344 | 1.997 | 2 | 7 | 1.093 | 7 | 15
| May | 112.769 | 342.7 | 1.645 | 3 | 5 | 2.7741 | 10 | 14 | 20.1 | 131.0941 | 1.295 | 4 | 6 | 1.555 | 11 | 15
| Jun | 2.735 | 578.3 | 0.805 | 9 | 5 | 3.2526 | 26 | 15 | 0 | 447.4956 | 0 |  |  | 2.101 | 26 | 15
| Jul | 4.839 | 568.4 | 0.599 | 25 | 6 | 3.3187 | 17 | 14 | 0 | 440.8962 | 0 |  |  | 2.14 | 17 | 15
| Aug | 1.368 | 658.2 | 0.572 | 10 | 7 | 4.1922 | 26 | 14 | 0 | 532.6434 | 0 |  |  | 2.632 | 26 | 15
| Sep | 51.756 | 724.8 | 1.229 | 28 | 24 | 5.086 | 30 | 14 | 2.1 | 517.8661 | 0.113 | 28 | 6 | 2.961 | 30 | 15
| Oct | 316.952 | 628.4 | 1.702 | 6 | 7 | 5.5767 | 18 | 14 | 80.5 | 296.188 | 1.201 | 6 | 7 | 3.039 | 1 | 15
| Nov | 598.664 | 394.3 | 3.255 | 26 | 8 | 5.4759 | 28 | 14 | 298.2 | 72.6701 | 2.427 | 1 | 7 | 1.982 | 6 | 15
| Dec | 698.704 | 433.3 | 3.171 | 31 | 24 | 5.537 | 1 | 14 | 329.8 | 62.0916 | 2.12 | 31 | 8 | 2.069 | 1 | 15
| Total | 4049.581 | 5822 | [6 empty] | 1726 | 2714
| Max |  |  | 3.255 |  |  | 5.65 |  |  |  |  | 2.551 |  |  | 3.039
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -30.2822 | 3.6876 | 0.75693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -27.4567 | 4.4245 | 0.16261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -33.8377 | 3.8943 | -1.4341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -37.567 | 3.6721 | -2.7015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 0 | 0 | 0 | -35.0231 | 3.6641 | -4.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 15 | 9.31 | 9.31 | 90 | 25.87 | 25.87 | -35.993 | 3.803 | -1.779 | 0 | 0 | 0 | 5.6 | 3.06 | 7.01 | 15.55 | 8.51 | 19.48
| 7 | 60 | 36.36 | 36.36 | 275 | 52.6 | 52.6 | -38.7016 | 4.3213 | 0.21141 | 0 | 0 | 0 | 21.85 | 11.96 | 27.38 | 31.61 | 17.3 | 39.61
| 8 | 111 | 66.16 | 66.07 | 479 | 79.83 | 79.83 | -35.4235 | 4.3945 | 1.1998 | 104.3 | 55.73 | 138.85 | 39.76 | 21.77 | 49.82 | 47.98 | 26.27 | 60.11
| 9 | 158 | 93.88 | 92.71 | 668 | 166.73 | 101.35 | -36.8689 | 4.9064 | 2.2849 | 325.7 | 176.5 | 409.45 | 56.42 | 30.88 | 70.69 | 66.84 | 36.47 | 89.08
| 10 | 195 | 116.03 | 113.11 | 827 | 296.45 | 117.44 | -36.1031 | 6.2008 | 5.0591 | 484.4 | 265.7 | 592.98 | 69.73 | 38.17 | 87.37 | 112.79 | 60.56 | 163.22
| 11 | 263 | 156.44 | 148.79 | 941 | 390.91 | 126.74 | -34.5636 | 6.9765 | 5.4079 | 593.5 | 327.31 | 719.04 | 94.02 | 51.47 | 117.8 | 166.86 | 88.94 | 238.46
| 12 | 278 | 165.66 | 158.81 | 1003 | 441.65 | 130.36 | -33.6763 | 6.2647 | 5.1147 | 653.9 | 361.31 | 788.87 | 99.56 | 54.5 | 124.74 | 201.93 | 107.5 | 283.59
| 13 | 277 | 165.04 | 159.18 | 1008 | 445.59 | 238.98 | -31.6698 | 4.1911 | 5.5711 | 665 | 367.54 | 801.72 | 99.19 | 54.3 | 124.27 | 204.75 | 109.01 | 287.12
| 14 | 259 | 154 | 154.61 | 955 | 401.73 | 475.13 | -33.2373 | 3.1788 | 4.9914 | 623.5 | 344.22 | 753.75 | 92.55 | 50.67 | 115.96 | 173.86 | 92.64 | 247.65
| 15 | 227 | 134.48 | 140.01 | 848 | 312.89 | 672.39 | -33.224 | 1.9243 | 6.0132 | 534.1 | 293.82 | 650.33 | 80.82 | 44.24 | 101.26 | 121.01 | 64.87 | 175.19
| 16 | 181 | 106.77 | 114.38 | 696 | 187.67 | 809.04 | -33.5 | 1.1489 | 5.4557 | 396.8 | 216.33 | 492.04 | 64.17 | 35.13 | 80.4 | 72.45 | 39.45 | 98.49
| 17 | 104 | 62.05 | 63.55 | 509 | 83.9 | 861.62 | -34.0382 | 3.2979 | 6.5386 | 210.3 | 112.91 | 272.44 | 37.29 | 20.41 | 46.72 | 50.43 | 27.6 | 63.18
| 18 | 53 | 32.2 | 32.2 | 306 | 57.72 | 806.87 | -36.3464 | 3.2977 | 5.6681 | 0 | 0 | 0 | 19.35 | 10.59 | 24.25 | 34.69 | 18.99 | 43.46
| 19 | 11 | 6.81 | 6.81 | 114 | 30.17 | 578.91 | -36.4727 | 2.4978 | 5.1895 | 0 | 0 | 0 | 4.09 | 2.24 | 5.13 | 18.13 | 9.92 | 22.72
| 20 | 0 | 0 | 0 | 0 | 0 | 0 | -36.913 | 1.9983 | 5.7177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -37.9742 | 2.0062 | 2.1391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -38.9062 | 1.8319 | 2.1388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -38.9555 | 0.95143 | 1.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.5188 | 0.95172 | 0.44827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.032 | 0 | 1.803 | 2.67 | 1.186 | 2.05 | 1.225 | 0.792 | 0 |  | 1.202 | 0.724 | 0 | 0 | 0 | -0.017 | -0.449 | -0.422 | -0.223 | -0.241 | -0.821 | -0.77 | 12.7 | 18.1
| 2 | 2.042 | 0 | 1.782 | 2.694 | 1.246 | 2.059 | 1.264 | 0.928 | 0 |  | 1.224 | 0.814 | 0 | 0 | 0 | 0 | -0.286 | -0.302 | -0.069 | -0.119 | -0.701 | -0.642 | 10.1 | 17.7
| 3 | 2.123 | 0.459 | 1.82 | 2.819 | 1.341 | 2.139 | 1.356 | 1.063 | 0 |  | 1.323 | 0.942 | 0 | 0 | 0 | 0 | -0.155 | -0.209 | -0.012 | -0.037 | -0.574 | -0.541 | 10 | 17.2
| 4 | 2.228 | 1.053 | 1.881 | 2.973 | 1.44 | 2.243 | 1.453 | 1.187 | 0 |  | 1.408 | 1.054 | 0 | 0 | 0 | 0 | -0.017 | -0.115 | 0 | 0 | -0.483 | -0.434 | 10 | 16.7
| 5 | 2.307 | 1.231 | 1.923 | 3.088 | 1.514 | 2.321 | 1.526 | 1.296 | 0 |  | 1.439 | 1.142 | 0 | 0 | 0 | 0 | 0.11 | -0.023 | 0 | 0 | -0.4127 | -0.328 | 10 | 16.3
| 6 | 2.358 | 1.272 | 1.952 | 3.145 | 1.565 | 2.373 | 1.577 | 1.412 | 0 | 0.072 | 1.445 | 1.221 | 0 | 0 | 0 | 0 | 0.048 | -0.05 | 0 | 0 | -0.4064 | -0.33 | 10 | 15.8
| 7 | 2.385 | 1.306 | 1.969 | 3.154 | 1.591 | 2.401 | 1.604 | 1.54 | 0 | 0.211 | 1.459 | 1.285 | 0 | 0 | 0 | 0 | -0.274 | -0.242 | 0 | 0 | -0.5304 | -0.462 | 10 | 15.4
| 8 | 2.101 | 3.487 | 1.804 | 2.796 | 1.327 | 2.118 | 1.34 | 1.45 | 1.097 | 0.078 | 1.294 | 1.157 | 0 | 0 | 0 | 0 | -0.664 | -0.499 | 0 | -0.071 | -0.7226 | -0.626 | 15 | 17.6
| 9 | 1.048 | 3.024 | 1.191 | 1.524 | 0.532 | 1.068 | 0.363 | 0.724 | 1.669 |  | 1.0285 | 0.53 | 0 | 0 | 0 | 0 | -1.032 | -0.773 | -0.128 | -0.236 | -0.9494 | -0.811 | 20 | 20
| 10 | 0.139 | 0.185 | 0.37 | 0.298 | 0 | -0.479 | -1.088 | 0.149 | 0.62 |  | 0.106 | -0.675 | -0.332 | -0.141 | -0.324 | -0.291 | -1.499 | -1.133 | -0.453 | -0.487 | -1.2632 | -1.077 | 21.3 | 20
| 11 | -0.07 | -0.068 | 0 | 0 | -0.759 | -1.956 | -2.496 | 0 | 0.047 |  | -0.8215 | -1.617 | -1.246 | -0.797 | -1.402 | -0.988 | -2.125 | -1.62 | -0.771 | -0.832 | -1.71 | -1.447 | 24.8 | 20.7
| 12 | -1.616 | -1.581 | 0 | -1.564 | -2.604 | -3.25 | -3.726 | 0 | 0 | -0.068 | -1.6695 | -2.518 | -2.078 | -1.474 | -2.485 | -1.632 | -2.709 | -2.108 | -1.234 | -1.184 | -2.024 | -1.687 | 27 | 22.2
| 13 | -3.561 | -3.487 | -0.545 | -3.679 | -4.128 | -4.289 | -4.673 | 0 | 0 | -0.668 | -2.3805 | -3.021 | -2.457 | -1.707 | -2.996 | -2.018 | -3.08 | -2.48 | -1.545 | -1.422 | -2.243 | -1.884 | 27 | 23.9
| 14 | -4.028 | -3.945 | -1.376 | -4.214 | -4.575 | -4.731 | -5.066 | 0 | 0 | -1.302 | -2.566 | -3.186 | -2.618 | -1.809 | -3.234 | -2.189 | -3.24 | -2.649 | -1.667 | -1.553 | -2.346 | -1.984 | 27 | 25.2
| 15 | -3.839 | -3.759 | -1.55 | -3.989 | -4.445 | -4.545 | -4.931 | -0.128 | 0 | -1.555 | -2.464 | -3.042 | -2.588 | -1.824 | -3.202 | -2.124 | -3.208 | -2.582 | -1.652 | -1.593 | -2.342 | -1.971 | 27 | 25.9
| 16 | -3.244 | -3.243 | -1.192 | -3.33 | -3.918 | -3.952 | -4.405 | -0.128 | 0 | -1.453 | -2.206 | -2.718 | -2.388 | -1.741 | -2.922 | -1.896 | -3.006 | -2.354 | -1.581 | -1.517 | -2.25 | -1.872 | 27 | 25.8
| 17 | -2.197 | -2.215 | -0.576 | -2.176 | -2.906 | -2.904 | -3.392 | 0 | 0 | -0.73 | -1.521 | -2.122 | -2.096 | -1.567 | -2.521 | -1.645 | -2.716 | -2.106 | -1.472 | -1.417 | -2.131 | -1.763 | 27 | 24.6
| 18 | -0.779 | -0.786 | -0.102 | -0.736 | -1.436 | -1.365 | -1.92 | 0 | 0 | -0.092 | -0.817 | -1.32 | -1.763 | -1.335 | -2.084 | -1.403 | -2.389 | -1.864 | -1.343 | -1.284 | -1.988 | -1.643 | 26.8 | 23.2
| 19 | 0 | 0 | 0 | 0 | -0.295 | 0.009 | -0.65 | 0 | 0 |  | -0.11 | -0.788 | -1.404 | -1.08 | -1.63 | -1.131 | -2.036 | -1.593 | -1.201 | -1.121 | -1.807 | -1.479 | 25.4 | 22.2
| 20 | 0 | 0 | 0.061 | 0.146 | 0 | 0.767 | 0.037 | 0 | 0 |  | 0.216 | -0.385 | -0.995 | -0.775 | -1.128 | -0.832 | -1.631 | -1.295 | -1.018 | -0.938 | -1.61 | -1.294 | 22.8 | 21.4
| 21 | 0.413 | 0.401 | 0.76 | 1.072 | 0 | 1.239 | 0.474 | 0 | 0 |  | 0.499 | -0.01 | -0.593 | -0.461 | -0.642 | -0.555 | -1.237 | -1.02 | -0.832 | -0.788 | -1.433 | -1.135 | 20 | 20.8
| 22 | 1.266 | 1.239 | 1.518 | 2.06 | 0 | 1.583 | 0.783 | 0 | 0.041 |  | 0.7242 | 0.164 | -0.32 | -0.247 | -0.314 | -0.363 | -0.974 | -0.83 | -0.661 | -0.638 | -1.281 | -1.041 | 20 | 20.2
| 23 | 1.814 | 1.781 | 1.701 | 2.396 | 0.333 | 1.841 | 1.011 | 0.183 | 0.243 |  | 0.96 | 0.42 | -0.138 | -0.107 | -0.097 | -0.224 | -0.798 | -0.691 | -0.492 | -0.512 | -1.15 | -0.967 | 20 | 19.6
| 24 | 1.988 | 0.082 | 1.801 | 2.613 | 0.92 | 2.007 | 1.167 | 0.342 | 0.202 |  | 1.158 | 0.618 | -0.027 | -0.022 | 0 | -0.097 | -0.634 | -0.562 | -0.371 | -0.387 | -1.009 | -0.881 | 16.8 | 18.8
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 13 | 15.4 | 21.7 | 23.4 | 27.4 | 26.6
| 2 | 10.3 | 14.8 | 20.1 | 22.2 | 24 | 25.8
| 3 | 7.9 | 14.2 | 19 | 21.3 | 20.8 | 24.9
| 4 | 5.7 | 13.6 | 17.8 | 20.3 | 17.8 | 24
| 5 | 3.8 | 13 | 16.6 | 19.3 | 15 | 23.2
| 6 | 2.1 | 12.4 | 16.6 | 19.3 | 12.4 | 22.4
| 7 | 0.7 | 11.8 | 18.2 | 20.5 | 10.1 | 21.8
| 8 | 0.1 | 11.2 | 20.3 | 22.1 | 8.7 | 21.4
| 9 | 1.7 | 11.8 | 22.3 | 23.4 | 9.5 | 22
| 10 | 6.1 | 13.4 | 24.9 | 24.5 | 13.1 | 23.5
| 11 | 12.5 | 15.7 | 28.3 | 25.8 | 19.1 | 25.5
| 12 | 20.2 | 18.4 | 32.3 | 27.4 | 26.7 | 27.8
| 13 | 28.5 | 21.3 | 36.2 | 28.7 | 35.2 | 30.2
| 14 | 36.1 | 23.2 | 39.7 | 29.8 | 43.4 | 32.3
| 15 | 41.9 | 24.8 | 42.5 | 30.6 | 50.2 | 33.8
| 16 | 45.4 | 25.4 | 44.4 | 31 | 55.1 | 34.6
| 17 | 46.3 | 24.6 | 45.4 | 31.4 | 57.3 | 34
| 18 | 44 | 23.5 | 41.7 | 31 | 56.3 | 32.9
| 19 | 39.5 | 22.6 | 35.5 | 30.3 | 53 | 32
| 20 | 34.4 | 21.9 | 31.7 | 29.1 | 48.8 | 31.2
| 21 | 29.3 | 20.8 | 28.6 | 28.1 | 44.3 | 30.3
| 22 | 24.6 | 20 | 26.5 | 27 | 39.8 | 29.4
| 23 | 20.2 | 19.2 | 25 | 26 | 35.4 | 28.4
| 24 | 16.3 | 18.1 | 23.5 | 24.9 | 31.2 | 27.4
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 3
| 1 | 13
| 2 | 32
| 3 | 41
| 4 | 57
| 5 | 63
| 6 | 67
| 7 | 87
| 8 | 97
| 9 | 104
| 10 | 155
| 11 | 151
| 12 | 142
| 13 | 156
| 14 | 170
| 15 | 166
| 16 | 211
| 17 | 199
| 18 | 211
| 19 | 257
| 20 | 318
| 21 | 263
| 22 | 269
| 23 | 273
| 24 | 260
| 25 | 308
| 26 | 339
| 27 | 330
| 28 | 341
| 29 | 409
| 30 | 382
| 31 | 426
| 32 | 433
| 33 | 391
| 34 | 332
| 35 | 291
| 36 | 244
| 37 | 184
| 38 | 167
| 39 | 145
| 40 | 102
| 41 | 76
| 42 | 41
| 43 | 27
| 44 | 22
| 45 | 5
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## CSE
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below. | [7 empty] | Note: Submitted CSE month formats don't match specified, if update
Keep VLOOKUP routine
MONTH |  | CODE | [6 empty] | See Rows 67, 127, 178, 500
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
[Note to Participants: Editorial changes: went with Hour 8 as example and 0n00 format (pertinent to Jan2018 discussion re Case 640)]
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracikng colors are:
Red is for edits from June 2013 through September 2017 distribution for the Round 3 sim trial draft.
Blue is for edits since Sep 2017 (since Sec5-2Aout-082917.xlsx):
editorial (not substantive) clarification re "hourly integrated"
| Software: | CSE
| Version: | 0.861.1
| Date of Results: | 2019-04-15 09:46:38.912566
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS | [7 empty] | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling | [7 empty] | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour |  | Month* | Day | Hour | kW | Month*
| 600 | 3.9928 | 5.9131 | 3.0202 | Jan | 1 | 1 | 6.481 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.481 | 1 |  | IF
| 610 | 4.0664 | 4.3818 | 3.0208 | Jan | 1 | 1 | 6.4322 | Dec | 1 | 14 |  | 1 | 1 | 1 | 6.4322 | 12
| 620 | 4.0936 | 4.0793 | 3.0379 | Jan | 1 | 1 | 4.4928 | Jun | 26 | 17 |  | 1 | 1 | 1 | 4.4928 | 6
| 630 | 4.3559 | 3.0204 | 3.0394 | Jan | 1 | 1 | 3.9983 | Jun | 26 | 18 |  | 1 | 1 | 1 | 3.9983 | 6 |  | Jan
| 640 | 2.4032 | 5.6439 | 4.2225 | Nov | 26 | 8 | 6.429 | Jan | 22 | 14 |  | 11 | 26 | 8 | 6.429 | 1 |  | Nov | VLOOKUP Table: Number to Mmm
| 650 | 0 | 4.6539 | 0 | Jan | 1 | 1 | 6.2897 | Dec | 1 | 14 |  | 1 | 1 | 1 | 6.2897 | 12
| 660 | 3.602 | 3.3397 | 2.7583 | Jan | 1 | 1 | 3.933 | Oct | 1 | 13 |  | 1 | 1 | 1 | 3.933 | 10 |  | 1 | Jan
| 670 | 5.3002 | 6.5777 | 3.6554 | Jan | 1 | 1 | 6.9253 | Oct | 1 | 13 |  | 1 | 1 | 1 | 6.9253 | 10 |  | 2 | Feb
| 680 | 1.7861 | 6.4298 | 1.7776 | Feb | 9 | 6 | 7.0513 | Jan | 22 | 14 |  | 2 | 9 | 6 | 7.0513 | 1 |  | 3 | Mar
| 685 | 4.5744 | 8.8592 | 3.0319 | Jan | 1 | 1 | 7.1594 | Jan | 22 | 14 |  | 1 | 1 | 1 | 7.1594 | 1 |  | 4 | Apr
| 695 | 2.4153 | 8.9741 | 1.7953 | Jan | 1 | 1 | 7.5407 | Jan | 22 | 14 |  | 1 | 1 | 1 | 7.5407 | 1 |  | 5 | May
| 900 | 1.3789 | 2.4638 | 2.4434 | Feb | 9 | 6 | 3.3764 | Oct | 1 | 14 |  | 2 | 9 | 6 | 3.3764 | 10 |  | 6 | Jun
| 910 | 1.6477 | 1.4149 | 2.469 | Feb | 9 | 6 | 2.7221 | Oct | 2 | 15 |  | 2 | 9 | 6 | 2.7221 | 10 |  | 7 | Jul
| 920 | 2.9561 | 2.7892 | 2.5124 | Feb | 9 | 6 | 3.0567 | Jun | 26 | 18 |  | 2 | 9 | 6 | 3.0567 | 6 |  | 8 | Aug
| 930 | 3.5236 | 2.075 | 2.537 | Feb | 9 | 6 | 2.6618 | Jun | 26 | 18 |  | 2 | 9 | 6 | 2.6618 | 6 |  | 9 | Sep
| 940 | 0.86324 | 2.3966 | 3.0519 | Jan | 1 | 9 | 3.3764 | Oct | 1 | 14 |  | 1 | 1 | 9 | 3.3764 | 10 |  | 10 | Oct
| 950 | 0 | 0.59803 | 0 | Jan | 1 | 1 | 2.3635 | Sep | 4 | 15 |  | 1 | 1 | 1 | 2.3635 | 9 |  | 11 | Nov
| 960 | 2.5221 | 0.92578 | 2.132 | Feb | 9 | 6 | 1.3771 | Jun | 26 | 17 |  | 2 | 9 | 6 | 1.3771 | 6 |  | 12 | Dec
| 980 | 0.24577 | 3.9953 | 1.2538 | Feb | 9 | 6 | 3.668 | Oct | 2 | 14 |  | 2 | 9 | 6 | 3.668 | 10
| 985 | 2.1202 | 6.2336 | 2.4522 | Feb | 9 | 6 | 4.2253 | Oct | 1 | 14 |  | 2 | 9 | 6 | 4.2253 | 10
| 995 | 0.75518 | 7.2022 | 1.3696 | Feb | 9 | 6 | 4.2238 | Jan | 22 | 15 |  | 2 | 9 | 6 | 4.2238 | 1
| 195 | 3.9901 | 0.60552 | 1.7907 | Jan | 1 | 1 | 0.99425 | Jun | 26 | 17 |  | 1 | 1 | 1 | 0.99425 | 6
| 200 | 4.8135 | 0.80024 | 2.226 | Nov | 26 | 8 | 1.2152 | Jun | 26 | 17 |  | 11 | 26 | 8 | 1.2152 | 6
| 210 | 5.9663 | 0.50307 | 2.629 | Jan | 1 | 2 | 0.94562 | Jun | 13 | 15 |  | 1 | 1 | 2 | 0.94562 | 6
| 215 | 5.3066 | 0.94579 | 2.42 | Nov | 26 | 8 | 1.3692 | Jun | 26 | 17 |  | 11 | 26 | 8 | 1.3692 | 6
| 220 | 6.6663 | 0.6106 | 2.8394 | Jan | 1 | 1 | 1.1085 | Jun | 13 | 15 |  | 1 | 1 | 1 | 1.1085 | 6
| 230 | 9.8124 | 0.99134 | 4.1329 | Jan | 1 | 1 | 1.7281 | Jun | 26 | 17 |  | 1 | 1 | 1 | 1.7281 | 6
| 240 | 5.4426 | 0.98237 | 2.6514 | Jan | 1 | 1 | 1.2947 | Jun | 13 | 15 |  | 1 | 1 | 1 | 1.2947 | 6
| 250 | 5.0438 | 3.429 | 2.8371 | Jan | 1 | 1 | 2.79 | Sep | 12 | 14 |  | 1 | 1 | 1 | 2.79 | 9
| 270 | 4.3465 | 7.2708 | 2.6114 | Jan | 1 | 2 | 7.011 | Jan | 22 | 14 |  | 1 | 1 | 2 | 7.011 | 1
| 280 | 4.5249 | 4.9963 | 2.6122 | Jan | 1 | 2 | 4.7651 | Jan | 22 | 14 |  | 1 | 1 | 2 | 4.7651 | 1
| 290 | 4.4242 | 5.6097 | 2.6115 | Jan | 1 | 2 | 6.8722 | Jan | 22 | 14 |  | 1 | 1 | 2 | 6.8722 | 1
| 300 | 4.3184 | 5.0551 | 2.6141 | Jan | 1 | 1 | 4.1631 | Jun | 26 | 17 |  | 1 | 1 | 1 | 4.1631 | 6
| 310 | 4.5803 | 3.7519 | 2.6149 | Jan | 1 | 1 | 3.7959 | Jun | 26 | 18 |  | 1 | 1 | 1 | 3.7959 | 6
| 320 | 3.6775 | 4.8585 | 2.609 | Jan | 1 | 1 | 6.4733 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.4733 | 1
| 395 | 4.855 | 0.007762 | 2.1574 | Jan | 1 | 2 | 0.3575 | Jun | 14 | 18 |  | 1 | 1 | 2 | 0.3575 | 6
| 400 | 6.5358 | 0.023304 | 2.8394 | Jan | 1 | 1 | 0.49365 | Jun | 14 | 15 |  | 1 | 1 | 1 | 0.49365 | 6
| 410 | 8.0451 | 0.048491 | 3.4407 | Jan | 1 | 1 | 0.69988 | Jun | 26 | 18 |  | 1 | 1 | 1 | 0.69988 | 6
| 420 | 6.8345 | 0.14062 | 3.2562 | Jan | 1 | 1 | 0.90853 | Jun | 26 | 18 |  | 1 | 1 | 1 | 0.90853 | 6
| 430 | 5.454 | 0.90616 | 3.2539 | Jan | 1 | 1 | 1.8398 | Jun | 26 | 15 |  | 1 | 1 | 1 | 1.8398 | 6
| 440 | 4.1559 | 3.9853 | 3.0272 | Jan | 1 | 1 | 4.6655 | Oct | 1 | 13 |  | 1 | 1 | 1 | 4.6655 | 10
| 450 | 3.9904 | 5.689 | 2.9783 | Jan | 1 | 1 | 6.1798 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.1798 | 1
| 460 | 4.0555 | 5.9398 | 2.9714 | Jan | 1 | 1 | 6.2429 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.2429 | 1
| 470 | 3.8995 | 5.6439 | 3.0007 | Jan | 1 | 1 | 6.3877 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.3877 | 1
| 800 | 4.9057 | 0.37983 | 2.7776 | Feb | 9 | 6 | 1.1019 | Aug | 5 | 15 |  | 2 | 9 | 6 | 1.1019 | 8
| 810 | 2.0375 | 1.4807 | 2.5001 | Feb | 9 | 6 | 2.4105 | Sep | 4 | 15 |  | 2 | 9 | 6 | 2.4105 | 9
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes | [7 empty] | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum | [7 empty] | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour |  | Month* | Day | Hour | °C | Month*
| 600FF | 25.5736 | -12.8904 | Feb | 9 | 7 | 68.3608 | Oct | 1 | 16 |  | 2 | 9 | 7 | 67.8478 | 10
| 900FF | 25.6921 | 2.1647 | Feb | 9 | 7 | 45.1138 | Sep | 4 | 15 |  | 2 | 9 | 7 | 44.7403 | 9
| 650FF | 18.4599 | -17.7616 | Jan | 1 | 1 | 66.8465 | Oct | 1 | 16 |  | 1 | 1 | 1 | 66.4036 | 10
| 950FF | 14.7096 | -13.2443 | Jan | 1 | 1 | 36.7765 | Sep | 11 | 15 |  | 1 | 1 | 1 | 36.6444 | 9
| 680FF | 33.1103 | -6.1966 | Feb | 9 | 7 | 78.5143 | Jan | 22 | 16 |  | 2 | 9 | 7 | 78.4503 | 1
| 980FF | 33.2952 | 12.5361 | Nov | 4 | 7 | 52.2464 | Sep | 12 | 15 |  | 11 | 4 | 7 | 51.9433 | 9
| 960 | 28.5573 | 8.0165 | Feb | 9 | 8 | 48.9033 | Oct | 2 | 16 |  | 2 | 9 | 8 | 48.5662 | 10
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1662.5278
| NORTH | 399.0475
| EAST | 1026.9874
| SOUTH | 1316.9162
| WEST | 903.0665
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 825.5194
| 660/South | 501.3136
| 670/South | 987.8182
620/West
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 665.2609
630/West
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -3.9307 | -46.2246 | Dec | 31 | 24 | 30.0812 | Jun | 13 | 15 |  | 12 | 31 | 24 | 30.0812 | 6
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 655.585 | 554.0235 | 3.0202 | 1 | 1 | 6.481 | 22 | 14 | 206.1043 | 67.8041 | 2.0774 | 1 | 5 | 2.2416 | 22 | 15
| Feb | 626.2627 | 394.2972 | 2.8997 | 9 | 6 | 5.3928 | 15 | 14 | 243.2297 | 15.1117 | 2.4434 | 9 | 6 | 0.99617 | 15 | 15
| Mar | 435.7419 | 474.3508 | 2.0344 | 17 | 6 | 5.1483 | 24 | 13 | 102.4399 | 68.5488 | 1.6129 | 17 | 6 | 1.4341 | 24 | 15
| Apr | 456.9543 | 220.1356 | 2.2073 | 11 | 6 | 4.0151 | 27 | 14 | 222.3692 | 12.3134 | 1.7706 | 3 | 4 | 0.63116 | 19 | 14
| May | 127.7958 | 321.1602 | 1.5922 | 1 | 5 | 3.0796 | 21 | 14 | 33.3469 | 117.8126 | 1.1425 | 1 | 5 | 1.4272 | 21 | 14
| Jun | 11.6999 | 497.4498 | 0.77848 | 9 | 5 | 3.2488 | 13 | 13 | 0 | 372.2992 | 0 | 1 | 1 | 1.8967 | 14 | 14
| Jul | 11.5431 | 505.8671 | 0.53975 | 26 | 5 | 3.2903 | 17 | 14 | 0 | 380.4363 | 0 | 1 | 1 | 1.943 | 17 | 14
| Aug | 6.9186 | 606.5032 | 0.55338 | 17 | 6 | 4.1195 | 8 | 14 | 0 | 485.6761 | 0 | 1 | 1 | 2.4852 | 5 | 14
| Sep | 74.3067 | 705.1929 | 1.1204 | 29 | 1 | 5.4503 | 2 | 14 | 0 | 484.0294 | 0 | 1 | 1 | 3.1368 | 4 | 14
| Oct | 328.4088 | 676.133 | 1.6237 | 15 | 6 | 6.2702 | 1 | 13 | 65.0694 | 305.5693 | 1.1882 | 7 | 7 | 3.3764 | 1 | 14
| Nov | 575.553 | 454.7409 | 2.8502 | 26 | 8 | 6.149 | 28 | 13 | 251.5988 | 80.4854 | 2.0863 | 26 | 8 | 2.2328 | 20 | 15
| Dec | 681.9851 | 503.27 | 2.9413 | 31 | 24 | 6.45 | 1 | 14 | 254.733 | 73.7394 | 1.9268 | 31 | 8 | 2.1054 | 1 | 15
| Total | 3992.755 | 5913.1242 | [6 empty] | 1378.8913 | 2463.8258
| Max |  |  | 3.0202 |  |  | 6.481 |  |  |  |  | 2.4434 |  |  | 3.3764
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -22.8397 | 0.38605 | 0.90277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -26.6414 | 0.40933 | 0.31055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -28.0897 | 0.32324 | -0.83045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -33.7622 | 0.019551 | -2.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 1.4992 | 0.54029 | 0.54029 | -35.2444 | -0.026626 | -3.5856 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34752 | 0.21439 | 0.41726
| 6 | 15.0006 | 9.0004 | 9.0004 | 82.0455 | 15.3297 | 15.3297 | -35.6508 | -0.077933 | -2.9391 | 0 | 0 | 0 | 5.76 | 3.544 | 6.9223 | 9.793 | 6.0253 | 11.7918
| 7 | 60.0025 | 36.0015 | 36.0015 | 264.1993 | 34.4328 | 34.4328 | -37.5801 | 0.1937 | -0.80157 | 0 | 0 | 0 | 23.0255 | 14.1619 | 27.6826 | 21.8537 | 13.4169 | 26.3554
| 8 | 111.0047 | 66.6028 | 66.6028 | 465.8199 | 55.5566 | 55.5479 | -37.0009 | 0.43445 | 0.63558 | 82.0324 | 50.937 | 107.13 | 42.4983 | 26.0993 | 51.1502 | 35.0242 | 21.4445 | 42.3184
| 9 | 158.0065 | 94.8038 | 94.8038 | 656.5745 | 139.4762 | 75.5077 | -36.328 | 0.70848 | 1.6749 | 297.541 | 180.8792 | 362.8681 | 60.5559 | 37.2213 | 72.8793 | 52.8909 | 32.3826 | 67.7615
| 10 | 195.008 | 117.0048 | 117.0048 | 816.0523 | 272.6453 | 91.9039 | -36.5645 | 1.807 | 3.6938 | 459.7525 | 278.4931 | 545.2226 | 74.7815 | 46.0006 | 90.0133 | 106.0912 | 66.3123 | 144.8439
| 11 | 263.0108 | 157.8065 | 157.8065 | 931.7134 | 372.0415 | 103.7499 | -35.3739 | 3.0787 | 5.1376 | 578.5582 | 348.905 | 675.1871 | 100.3258 | 61.4812 | 121.0763 | 171.3254 | 107.1366 | 229.0314
| 12 | 278.0116 | 166.8069 | 166.8069 | 996.141 | 427.7583 | 110.2849 | -34.1943 | 3.2866 | 5.1381 | 652.8082 | 391.0585 | 749.7897 | 105.248 | 64.2908 | 127.4075 | 214.7217 | 133.6999 | 280.7528
| 13 | 277.0115 | 166.2068 | 166.2068 | 1002.0363 | 433.4522 | 207.6793 | -32.6854 | 2.1422 | 5.2613 | 673.3877 | 404.3853 | 768.3238 | 104.1118 | 63.1249 | 126.1131 | 213.836 | 132.4799 | 281.1221
| 14 | 259.0108 | 155.4066 | 155.4066 | 951.5143 | 389.6588 | 443.3988 | -32.6302 | 0.78812 | 5.1527 | 628.6623 | 377.3723 | 720.0014 | 97.1633 | 58.8997 | 117.7605 | 181.0836 | 112.4723 | 242.0489
| 15 | 227.0095 | 136.2054 | 136.2054 | 847.7872 | 300.3721 | 644.8859 | -33.3209 | -0.62158 | 5.4585 | 528.0285 | 316.992 | 613.0512 | 85.3291 | 51.7282 | 103.3009 | 121.3543 | 75.3683 | 166.4995
| 16 | 181.0076 | 108.6046 | 108.6046 | 697.2651 | 174.1119 | 787.9666 | -33.4665 | -0.73525 | 5.6185 | 378.3411 | 229.4327 | 452.897 | 68.2121 | 41.4256 | 82.5129 | 63.7931 | 38.9794 | 83.7436
| 17 | 104.0043 | 62.4026 | 62.4026 | 511.7801 | 64.3006 | 850.1509 | -33.8865 | -0.44746 | 5.9695 | 191.9413 | 117.7938 | 241.2176 | 39.5371 | 24.1701 | 47.709 | 37.6588 | 22.8693 | 45.4814
| 18 | 53.0022 | 31.8013 | 31.8013 | 309.2767 | 39.0057 | 805.1397 | -35.3916 | -0.64839 | 5.9794 | 14.3991 | 9.06 | 19.1922 | 20.2628 | 12.4348 | 24.4004 | 24.2426 | 14.709 | 29.321
| 19 | 11.0004 | 6.6003 | 6.6003 | 116.1785 | 18.8437 | 590.3427 | -36.4941 | -0.91461 | 5.3256 | 0 | 0 | 0 | 4.2104 | 2.5852 | 5.0665 | 11.6997 | 7.1153 | 14.1359
| 20 | 0 | 0 | 0 | 5.5971 | 1.841 | 78.5987 | -36.7865 | -1.4056 | 5.4067 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1413 | 0.69581 | 1.3866
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -37.563 | -1.607 | 3.6698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -38.5529 | -1.9502 | 2.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -38.9993 | -2.8551 | 1.7227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.7814 | -3.3493 | 0.85954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 1.8838 | 0.00043451 | 1.6843 | 2.3394 | 0.99585 | 1.9212 | 1.145 | 0.71655 | 0 | 0 | 0.9489 | 0.32105 | 0 | 0 | 0 | 0 | -0.049027 | -0.13418 | -0.052736 | -0.18841 | -0.64521 | -0.57478 | 11.1142 | 16.6192
| 2 | 1.9935 | 0.39261 | 1.779 | 2.4806 | 1.1111 | 2.0146 | 1.2047 | 0.84236 | 0 | 0 | 1.0473 | 0.40368 | 0 | 0 | 0 | 0 | 0.02692 | -0.081538 | -0.0012209 | -0.13027 | -0.55887 | -0.51269 | 10 | 16.0221
| 3 | 2.0547 | 0.80293 | 1.8309 | 2.5674 | 1.1938 | 2.0666 | 1.2518 | 0.94623 | 0 | 0 | 1.1317 | 0.47533 | 0 | 0 | 0 | 0 | 0.11975 | -0.026795 | 0 | -0.068221 | -0.46354 | -0.44442 | 10 | 15.4654
| 4 | 2.1202 | 1.034 | 1.8839 | 2.6744 | 1.2656 | 2.1268 | 1.3012 | 1.0458 | 0 | 0 | 1.2243 | 0.55403 | 0 | 0 | 0.001611 | 0 | 0.24941 | 0.034874 | 0 | -0.0086705 | -0.3547 | -0.36915 | 10 | 14.9003
| 5 | 2.1532 | 1.1731 | 1.9135 | 2.7158 | 1.2984 | 2.1569 | 1.3204 | 1.1187 | 0 | 0 | 1.2901 | 0.60291 | 0 | 0 | 0.20148 | 0 | 0.34005 | 0.098044 | 0 | 0 | -0.26008 | -0.29783 | 10 | 14.3857
| 6 | 2.1631 | 1.2448 | 1.9223 | 2.7285 | 1.3219 | 2.1651 | 1.3355 | 1.1879 | 0 | 0 | 1.351 | 0.64819 | 0 | 0 | 0.20839 | 0 | 0.23558 | 0.064405 | 0 | 0 | -0.25356 | -0.30657 | 10 | 13.9037
| 7 | 2.1843 | 1.3018 | 1.9415 | 2.7542 | 1.3375 | 2.1854 | 1.3459 | 1.2589 | 0 | 0 | 1.4134 | 0.68594 | 0 | 0 | 0.0044408 | 0 | -0.1131 | -0.089405 | 0 | -0.018269 | -0.35224 | -0.38991 | 10 | 13.4247
| 8 | 1.7765 | 3.0205 | 1.6726 | 2.2606 | 1.0054 | 1.777 | 1.0098 | 1.0863 | 0.90177 | 0 | 1.226 | 0.52924 | 0 | 0 | 0 | 0 | -0.4792 | -0.3116 | 0 | -0.11586 | -0.49552 | -0.48515 | 15.5 | 15.9016
| 9 | 0.5478 | 1.6521 | 0.80151 | 0.84369 | 0.17368 | 0.54801 | 0.059474 | 0.53703 | 1.1161 | 0 | 0.63568 | 0.086248 | 0 | 0 | 0 | 0 | -0.89805 | -0.61456 | -0.070157 | -0.24815 | -0.68807 | -0.62671 | 20 | 20
| 10 | 0 | 0.075395 | 0.082875 | 0.0024258 | -0.053007 | -0.95761 | -1.666 | 0.11777 | 0.49385 | 0 | 0.19897 | -0.50421 | -0.16869 | -0.059292 | -0.19006 | -0.18419 | -1.5518 | -1.1481 | -0.36695 | -0.50733 | -1.0367 | -0.92083 | 20.7841 | 20
| 11 | -0.92066 | -0.40515 | 0 | -0.99799 | -1.9332 | -2.8606 | -3.5885 | 0 | 0.066615 | -0.028774 | -0.34013 | -1.1965 | -1.2347 | -0.78553 | -1.5089 | -1.0716 | -2.3959 | -1.8678 | -0.76666 | -0.86339 | -1.4712 | -1.2898 | 26.0342 | 20.1042
| 12 | -3.0739 | -2.6298 | -0.45456 | -3.2655 | -4.069 | -4.335 | -5.0849 | 0 | 0 | -0.56154 | -0.98196 | -1.8905 | -2.2634 | -1.5756 | -2.7261 | -1.9293 | -3.1327 | -2.5371 | -1.1411 | -1.1778 | -1.8619 | -1.6114 | 27 | 21.6771
| 13 | -4.364 | -4.1733 | -1.6509 | -4.6214 | -5.3127 | -5.2497 | -5.993 | 0 | 0 | -1.192 | -1.5878 | -2.4977 | -2.7049 | -1.9242 | -3.2555 | -2.4066 | -3.4278 | -2.9109 | -1.3558 | -1.3736 | -2.0803 | -1.8125 | 27 | 23.7146
| 14 | -4.6667 | -4.592 | -2.1461 | -4.8903 | -5.5694 | -5.3818 | -6.0919 | 0 | 0 | -1.5455 | -1.9023 | -2.7863 | -2.7504 | -2.0023 | -3.3127 | -2.4752 | -3.4049 | -2.9258 | -1.4518 | -1.4517 | -2.1666 | -1.888 | 27 | 24.982
| 15 | -4.0529 | -4.0239 | -1.9151 | -4.1429 | -5.054 | -4.6926 | -5.5054 | -0.02487 | 0 | -1.6506 | -1.9331 | -2.8206 | -2.449 | -1.8527 | -2.9394 | -2.1675 | -3.0702 | -2.5909 | -1.3908 | -1.3713 | -2.0876 | -1.8001 | 27 | 25.2873
| 16 | -2.8873 | -2.8759 | -1.281 | -2.8645 | -3.941 | -3.486 | -4.3565 | -0.0054093 | 0 | -1.5424 | -1.7333 | -2.6157 | -1.9631 | -1.5702 | -2.2909 | -1.6634 | -2.5639 | -2.0688 | -1.2243 | -1.1792 | -1.8986 | -1.5962 | 27 | 25.2471
| 17 | -1.329 | -1.3246 | -0.38043 | -1.1447 | -2.3532 | -1.8707 | -2.7253 | 0 | 0 | -1.1511 | -1.2638 | -2.1061 | -1.5159 | -1.2726 | -1.6885 | -1.2613 | -2.101 | -1.6542 | -1.0839 | -1.0349 | -1.7366 | -1.4401 | 27 | 24.4059
| 18 | -0.036587 | -0.036104 | 0 | 0 | -0.51365 | -0.062132 | -0.87523 | 0 | 0 | -0.46865 | -0.54502 | -1.3534 | -1.1667 | -1.0133 | -1.2498 | -0.97604 | -1.7475 | -1.3655 | -0.97268 | -0.93142 | -1.612 | -1.3312 | 25.7064 | 22.6175
| 19 | 0.047689 | 0.048108 | 0.068677 | 0.3733 | 0 | 1.0222 | 0.15843 | 0 | 0 | -0.10765 | -0.13333 | -0.91496 | -0.84578 | -0.76378 | -0.8713 | -0.7202 | -1.4176 | -1.1029 | -0.8477 | -0.81522 | -1.4718 | -1.2069 | 21.3714 | 21.3767
| 20 | 0.87302 | 0.87401 | 0.85087 | 1.5232 | 0 | 1.6012 | 0.60708 | 0 | 0 | 0 | 0.11696 | -0.64822 | -0.48174 | -0.45877 | -0.45588 | -0.4781 | -1.0309 | -0.84841 | -0.71147 | -0.69185 | -1.3161 | -1.0712 | 20 | 20.564
| 21 | 1.5518 | 1.5523 | 1.4115 | 2.1392 | 0.064176 | 1.9179 | 0.89914 | 0 | 0.086615 | 0 | 0.34273 | -0.42283 | -0.1626 | -0.17946 | -0.099993 | -0.27107 | -0.69086 | -0.63671 | -0.58603 | -0.58322 | -1.1782 | -0.95683 | 20 | 20.0224
| 22 | 1.9363 | 1.9366 | 1.7543 | 2.4968 | 0.54736 | 2.1437 | 1.1068 | 0 | 0.33452 | 0 | 0.54685 | -0.23074 | -0.010249 | -0.026977 | 0 | -0.12549 | -0.49742 | -0.49022 | -0.48581 | -0.49948 | -1.0709 | -0.87231 | 20 | 20
| 23 | 2.1702 | 2.1703 | 1.9598 | 2.7218 | 0.88344 | 2.2881 | 1.2559 | 0.081877 | 0.54165 | 0 | 0.71216 | -0.065507 | 0 | 0 | 0 | -0.025991 | -0.37088 | -0.38407 | -0.39359 | -0.42484 | -0.97062 | -0.79533 | 20 | 20
| 24 | 2.2658 | 0 | 2.0439 | 2.8049 | 1.0938 | 2.3327 | 1.3349 | 0.29481 | 0 | 0 | 0.82345 | 0.055548 | 0 | 0 | 0 | 0 | -0.25271 | -0.28879 | -0.28879 | -0.33992 | -0.85843 | -0.70925 | 12.9579 | 18.1003
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 7.3199 | 14.7379 | 19.8311 | 21.2148 | 19.3025 | 27.6665
| 2 | 5.475 | 14.2075 | 19.0165 | 20.7077 | 17.2859 | 27.1526
| 3 | 3.8429 | 13.7002 | 18.1137 | 20.0478 | 15.4125 | 26.66
| 4 | 2.3514 | 13.1833 | 16.994 | 19.188 | 13.6262 | 26.1515
| 5 | 1.0503 | 12.7111 | 15.8658 | 18.2994 | 11.9969 | 25.6862
| 6 | -0.033328 | 12.2668 | 16.1929 | 18.5567 | 10.5252 | 25.2544
| 7 | -1.0231 | 11.8353 | 18.4147 | 20.0938 | 9.1662 | 24.8308
| 8 | -0.98405 | 11.941 | 20.1417 | 22.4421 | 8.8545 | 24.9686
| 9 | 2.4994 | 13.2165 | 22.2539 | 23.5009 | 11.6688 | 26.3146
| 10 | 9.5334 | 15.2859 | 25.3076 | 24.6745 | 17.8327 | 28.2183
| 11 | 17.965 | 17.5497 | 29.4735 | 26.1394 | 25.8327 | 30.208
| 12 | 26.9295 | 19.8553 | 34.0869 | 27.5275 | 34.849 | 32.2226
| 13 | 35.5894 | 22.0025 | 38.0756 | 28.5007 | 43.9435 | 34.0812
| 14 | 42.8259 | 23.2661 | 41.1874 | 29.1549 | 51.6986 | 35.3862
| 15 | 47.0783 | 23.5646 | 43.0949 | 29.3989 | 57.0436 | 35.9936
| 16 | 48.2109 | 23.5055 | 43.7728 | 29.2893 | 59.5967 | 36.0431
| 17 | 45.9023 | 22.7021 | 43.4747 | 29.1458 | 58.7261 | 35.2665
| 18 | 39.9832 | 20.9392 | 42.6822 | 29.0474 | 54.2792 | 33.6073
| 19 | 33.3 | 19.7278 | 34.1248 | 28.666 | 49.0597 | 32.4976
| 20 | 27.5274 | 18.9536 | 30.7295 | 27.3534 | 44.294 | 31.7818
| 21 | 22.5321 | 18.2399 | 27.846 | 26.0894 | 39.9085 | 31.126
| 22 | 18.1055 | 17.5304 | 25.8648 | 25.2973 | 35.8862 | 30.5149
| 23 | 14.1487 | 16.8299 | 24.4442 | 24.6727 | 32.1123 | 29.9001
| 24 | 10.8188 | 16.228 | 22.9121 | 23.7451 | 28.6933 | 29.355
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 0
| 1 | 0
| 2 | 4
| 3 | 7
| 4 | 23
| 5 | 25
| 6 | 36
| 7 | 44
| 8 | 65
| 9 | 74
| 10 | 98
| 11 | 117
| 12 | 148
| 13 | 211
| 14 | 206
| 15 | 208
| 16 | 255
| 17 | 288
| 18 | 253
| 19 | 329
| 20 | 365
| 21 | 323
| 22 | 327
| 23 | 316
| 24 | 283
| 25 | 286
| 26 | 299
| 27 | 287
| 28 | 319
| 29 | 340
| 30 | 362
| 31 | 417
| 32 | 429
| 33 | 417
| 34 | 390
| 35 | 335
| 36 | 272
| 37 | 210
| 38 | 150
| 39 | 77
| 40 | 60
| 41 | 40
| 42 | 30
| 43 | 21
| 44 | 11
| 45 | 3
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## DeST
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracking colors are:
Red is for edits from June 2013 through April 2018 distribution for the Round 3 sim trial draft.
| Software: | DeST | DeST
| Version: |  | 2.0-20190401
| Date of Results: |  | May 20. 2019
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.047 | 5.432 | 3.035 | Jan | 1 | 0 | 5.422 | Jan | 22 | 14
| 610 | 4.144 | 4.173 | 3.039 | Jan | 1 | 0 | 5.331 | Jan | 22 | 14
| 620 | 4.297 | 3.909 | 3.068 | Jan | 1 | 0 | 3.955 | Jun | 26 | 17
| 630 | 4.677 | 2.787 | 3.072 | Jan | 1 | 0 | 3.526 | Jun | 26 | 17
| 640 | 2.619 | 5.237 | 4.658 | Nov | 26 | 7 | 5.365 | Jan | 22 | 14
| 650 | 0 | 4.186 | 0 |  |  |  | 5.045 | Oct | 18 | 14
| 660 | 3.821 | 3.26 | 2.798 | Jan | 1 | 0 | 3.355 | Oct | 11 | 14
| 670 | 5.573 | 5.954 | 3.812 | Jan | 1 | 0 | 5.839 | Oct | 10 | 13
| 680 | 1.732 | 5.932 | 1.811 | Jan | 1 | 1 | 5.861 | Jan | 22 | 14
| 685 | 4.646 | 8.238 | 3.054 | Jan | 1 | 0 | 6.071 | Jan | 22 | 14
| 695 | 2.385 | 8.386 | 1.855 | Jan | 1 | 1 | 6.355 | Jan | 22 | 14
| 900 | 1.591 | 2.383 | 2.453 | Feb | 9 | 5 | 2.556 | Sep | 11 | 14
| 910 | 1.86 | 1.49 | 2.474 | Feb | 9 | 5 | 2.103 | Oct | 12 | 14
| 920 | 3.259 | 2.706 | 2.513 | Feb | 9 | 5 | 2.71 | Jun | 26 | 17
| 930 | 3.933 | 1.908 | 2.549 | Feb | 9 | 5 | 2.335 | Jun | 26 | 17
| 940 | 1.149 | 2.343 | 3.659 | Feb | 9 | 7 | 2.556 | Sep | 11 | 14
| 950 | 0 | 0.618 | 0 |  |  |  | 2.054 | Sep | 11 | 14
| 960 | 2.771 | 0.909 | 2.085 | Jan | 1 | 0 | 1.367 | Jun | 26 | 16
| 980 | 0.266 | 3.758 | 1.382 | Feb | 9 | 5 | 2.93 | Oct | 18 | 14
| 985 | 2.279 | 5.88 | 2.458 | Feb | 9 | 5 | 3.208 | Oct | 11 | 14
| 995 | 0.77 | 6.771 | 1.462 | Feb | 9 | 5 | 3.315 | Jan | 22 | 14
| 195 | 4.157 | 0.628 | 1.799 | Jan | 1 | 0 | 0.973 | Jun | 26 | 16
| 200 | 5.226 | 0.835 | 2.308 | Jan | 1 | 0 | 1.239 | Jun | 26 | 16
| 210 | 6.531 | 0.496 | 2.605 | Jan | 1 | 0 | 0.937 | Jun | 26 | 16
| 215 | 5.697 | 0.922 | 2.52 | Jan | 1 | 0 | 1.386 | Jun | 26 | 16
| 220 | 7.178 | 0.55 | 2.863 | Jan | 1 | 0 | 1.04 | Jun | 26 | 16
| 230 | 10.417 | 0.929 | 4.223 | Jan | 1 | 0 | 1.734 | Jun | 26 | 16
| 240 | 5.944 | 0.876 | 2.685 | Jan | 1 | 0 | 1.218 | Jun | 26 | 16
| 250 | 5.373 | 3.471 | 2.855 | Jan | 1 | 0 | 2.751 | Sep | 3 | 14
| 270 | 4.273 | 6.698 | 2.56 | Jan | 1 | 1 | 5.832 | Jan | 22 | 14
| 280 | 4.619 | 4.215 | 2.568 | Jan | 1 | 1 | 3.768 | Dec | 1 | 13
| 290 | 4.381 | 5.31 | 2.561 | Jan | 1 | 1 | 5.739 | Jan | 22 | 14
| 300 | 4.46 | 4.805 | 2.589 | Jan | 1 | 0 | 3.695 | Jun | 26 | 17
| 310 | 4.846 | 3.402 | 2.592 | Jan | 1 | 0 | 3.252 | Jun | 26 | 17
| 320 | 3.599 | 4.42 | 2.546 | Jan | 1 | 1 | 5.304 | Jan | 22 | 14
| 395 | 5.145 | 0.006 | 2.085 | Jan | 1 | 1 | 0.308 | Jun | 14 | 16
| 400 | 7.047 | 0.017 | 2.863 | Jan | 1 | 0 | 0.457 | Jun | 26 | 17
| 410 | 8.661 | 0.041 | 3.543 | Jan | 1 | 0 | 0.709 | Jun | 26 | 16
| 420 | 7.433 | 0.119 | 3.365 | Jan | 1 | 0 | 0.917 | Jun | 26 | 16
| 430 | 5.954 | 0.944 | 3.36 | Jan | 1 | 0 | 1.84 | Jun | 26 | 15
| 440 | 4.33 | 3.458 | 3.06 | Jan | 1 | 0 | 3.766 | Oct | 11 | 13
| 450 | 3.375 | 6.161 | 2.753 | Jan | 1 | 0 | 6.063 | Jan | 22 | 13
| 460 | 3.873 | 5.929 | 2.98 | Jan | 1 | 0 | 5.902 | Jan | 22 | 13
| 470 | 3.54 | 5.649 | 2.807 | Jan | 1 | 0 | 5.57 | Jan | 22 | 14
| 800 | 5.403 | 0.362 | 2.864 | Feb | 9 | 5 | 1.157 | Aug | 5 | 14
| 810 | 2.454 | 1.357 | 2.512 | Feb | 9 | 5 | 1.94 | Sep | 11 | 14
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 25.26 | -13.52 | Feb | 9 | 6 | 65 | Oct | 11 | 15
| 900FF | 25.25 | 1.31 | Feb | 9 | 7 | 44.46 | Sep | 11 | 15
| 650FF | 18.04 | -17.37 | Dec | 30 | 23 | 62.59 | Oct | 11 | 15
| 950FF | 14.35 | -13.36 | Dec | 30 | 23 | 36.37 | Sep | 11 | 15
| 680FF | 33.3 | -6.89 | Feb | 9 | 7 | 74.97 | Oct | 12 | 15
| 980FF | 33.3 | 12.4 | Nov | 5 | 6 | 52.81 | Oct | 21 | 14
| 960 | 29.45 | 6.74 | Feb | 9 | 6 | 53.18 | Oct | 20 | 14
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1667.158
| NORTH | 477.31
| EAST | 1016.676
| SOUTH | 1290.593
| WEST | 905.722
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 805.046
| 660/South | 506.461
| 670/South | 994.318
| 620/West | 569.394
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 663.345
| 630/West | 399.173
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -5.9 | -46.85 | Dec | 31 | 23 | 24.62 | Aug | 4 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 672.684 | 417.93 | 3.036 | 1 | 0 | 5.422 | 22 | 14 | 275.307 | 33.493 | 2.178 | 1 | 4 | 1.637 | 22 | 15
| Feb | 635.299 | 315.415 | 2.922 | 9 | 5 | 4.444 | 15 | 14 | 292.916 | 4.724 | 2.453 | 9 | 5 | 0.588 | 15 | 15
| Mar | 450.494 | 410.736 | 2.065 | 17 | 5 | 4.252 | 9 | 14 | 119.976 | 40.898 | 1.646 | 17 | 5 | 1.143 | 10 | 14
| Apr | 447.957 | 230.168 | 2.238 | 11 | 5 | 3.6 | 7 | 14 | 214.166 | 18.267 | 1.725 | 3 | 3 | 1.032 | 8 | 14
| May | 128 | 338.582 | 1.569 | 1 | 4 | 2.894 | 10 | 14 | 26.771 | 128.592 | 1.124 | 1 | 5 | 1.446 | 11 | 14
| Jun | 11.218 | 526.439 | 0.748 | 9 | 4 | 3.067 | 14 | 14 | 0 | 408.473 |  |  |  | 1.873 | 14 | 14
| Jul | 10.105 | 525.149 | 0.512 | 26 | 4 | 3.155 | 29 | 13 | 0 | 408.145 |  |  |  | 1.83 | 17 | 14
| Aug | 8.376 | 621.101 | 0.532 | 17 | 5 | 4.038 | 29 | 13 | 0 | 510.152 |  |  |  | 2.212 | 29 | 14
| Sep | 76.741 | 672.084 | 1.114 | 29 | 2 | 4.911 | 30 | 13 | 0 | 466.106 |  |  |  | 2.556 | 11 | 14
| Oct | 324.148 | 611.126 | 1.619 | 9 | 5 | 5.278 | 10 | 13 | 63.591 | 269.566 | 1.158 | 7 | 6 | 2.549 | 12 | 14
| Nov | 585.805 | 377.147 | 2.931 | 26 | 7 | 5.229 | 29 | 13 | 283.888 | 56.214 | 2.201 | 26 | 7 | 1.683 | 20 | 14
| Dec | 697.819 | 386.209 | 2.972 | 31 | 23 | 5.294 | 1 | 13 | 314.279 | 38.054 | 1.981 | 9 | 6 | 1.595 | 2 | 14
| Total | 4048.646 | 5432.086 | [6 empty] | 1590.894 | 2382.684
| Max |  |  | 3.036 |  |  | 5.422 |  |  |  |  | 2.453 |  |  | 2.556
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -30.28 | 3.69 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -27.46 | 4.42 | 0.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -33.84 | 3.89 | -1.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -37.57 | 3.67 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 1.17 | 0.7 | 0.7 | -35.02 | 3.66 | -4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 0.28 | 0.54
| 6 | 15 | 9 | 9 | 82.05 | 20.5 | 20.5 | -35.99 | 3.8 | -1.78 | 0 | 0 | 0 | 5.49 | 3.54 | 6.93 | 12.51 | 8.07 | 15.8
| 7 | 60 | 36 | 36 | 273.2 | 46 | 46 | -38.7 | 4.32 | 0.21 | 0 | 0 | 0 | 21.96 | 14.16 | 27.74 | 28.06 | 18.1 | 35.45
| 8 | 111 | 66.6 | 66.6 | 477.91 | 73.4 | 73.4 | -35.42 | 4.39 | 1.2 | 62.99 | 41.95 | 81.98 | 40.63 | 26.2 | 51.32 | 44.78 | 28.88 | 56.56
| 9 | 158 | 94.8 | 94.8 | 668 | 164.1 | 98.8 | -36.87 | 4.91 | 2.28 | 321.42 | 200.8 | 394.31 | 57.83 | 37.3 | 73.05 | 64.53 | 43.25 | 86.7
| 10 | 195 | 117 | 117 | 827 | 294.38 | 119.2 | -36.1 | 6.2 | 5.06 | 491.87 | 297.08 | 584.9 | 71.37 | 46.03 | 90.15 | 113.53 | 82.86 | 164.26
| 11 | 263 | 157.8 | 157.8 | 941 | 390.75 | 133.6 | -34.56 | 6.98 | 5.41 | 608.92 | 362.95 | 714.8 | 96.26 | 62.09 | 121.59 | 172.34 | 124.7 | 244.33
| 12 | 278 | 166.8 | 166.8 | 1003 | 443.74 | 141.3 | -33.68 | 6.26 | 5.11 | 673.56 | 399.66 | 786.82 | 101.75 | 65.63 | 128.53 | 211.22 | 149.98 | 293.03
| 13 | 277 | 166.2 | 166.2 | 1008 | 448.17 | 238.46 | -31.67 | 4.19 | 5.57 | 684.62 | 405.96 | 799.14 | 101.39 | 65.39 | 128.06 | 214.69 | 152.17 | 297.25
| 14 | 259 | 155.4 | 155.4 | 955 | 403.38 | 460.58 | -33.24 | 3.18 | 4.99 | 641 | 381.03 | 750.28 | 94.8 | 61.14 | 119.74 | 181.43 | 130.74 | 255.91
| 15 | 227 | 136.2 | 136.2 | 848 | 314 | 644.63 | -33.22 | 1.92 | 6.01 | 543.97 | 326.05 | 642.14 | 83.09 | 53.59 | 104.95 | 124.33 | 90.97 | 179.73
| 16 | 181 | 108.6 | 108.6 | 696 | 189.16 | 771.27 | -33.5 | 1.15 | 5.46 | 395.66 | 242.52 | 477 | 66.25 | 42.73 | 83.68 | 70.83 | 48.68 | 97.78
| 17 | 104 | 62.4 | 62.4 | 509 | 77.4 | 818.34 | -34.04 | 3.3 | 6.54 | 184.45 | 119.32 | 233.64 | 38.07 | 24.55 | 48.08 | 47.22 | 30.45 | 59.64
| 18 | 53 | 31.8 | 31.8 | 304.41 | 50.1 | 758.2 | -36.35 | 3.3 | 5.67 | 4.82 | 3.3 | 6.44 | 19.4 | 12.51 | 24.5 | 30.56 | 19.71 | 38.6
| 19 | 11 | 6.6 | 6.6 | 110.72 | 23.9 | 525.64 | -36.47 | 2.5 | 5.19 | 0 | 0 | 0 | 4.03 | 2.6 | 5.09 | 14.58 | 9.4 | 18.42
| 20 | 0 | 0 | 0 | 3.65 | 2 | 19.69 | -36.91 | 2 | 5.72 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 0.79 | 1.54
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -37.97 | 2.01 | 2.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -38.91 | 1.83 | 2.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -38.96 | 0.95 | 1.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.52 | 0.95 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 1.9869 | 0.025 | 1.835 | 2.545 | 1.044 | 2.033 | 1.202 | 1.0685 | 0 | 0 | 1.1713 | 0.40804 | 0 | 0 | 0 | 0 | 0 | -0.139 | -0.11986 | -0.28999 | -0.70663 | -0.6563 | 10 | 15.59
| 2 | 2.0692 | 0.611 | 1.901 | 2.631 | 1.154 | 2.096 | 1.253 | 1.1715 | 0 | 0 | 1.266 | 0.48876 | 0 | 0 | 0 | 0 | 0.078 | -0.074 | -0.038655 | -0.22559 | -0.62235 | -0.5916 | 10 | 15.02
| 3 | 2.1291 | 0.951 | 1.95 | 2.707 | 1.232 | 2.145 | 1.293 | 1.2675 | 0 | 0 | 1.3543 | 0.56563 | 0 | 0 | 0 | 0 | 0.158 | -0.009 | 0 | -0.15164 | -0.52812 | -0.5172 | 10 | 14.48
| 4 | 2.2065 | 1.19 | 2.017 | 2.81 | 1.301 | 2.216 | 1.34 | 1.3715 | 0 | 0 | 1.4513 | 0.64603 | 0 | 0 | 0.131 | 0 | 0.244 | 0.053 | 0 | -0.07752 | -0.43146 | -0.4428 | 10 | 13.9
| 5 | 2.243 | 1.321 | 2.048 | 2.851 | 1.332 | 2.249 | 1.356 | 1.4399 | 0 | 0 | 1.5133 | 0.69388 | 0 | 0 | 0.363 | 0 | 0.332 | 0.115 | 0 | -0.00322 | -0.33373 | -0.3681 | 10 | 13.43
| 6 | 2.2675 | 1.402 | 2.071 | 2.88 | 1.366 | 2.271 | 1.381 | 1.5162 | 0 | 0 | 1.5837 | 0.75613 | 0 | 0 | 0.33 | 0 | 0.247 | 0.057 | 0 | -0.03011 | -0.34526 | -0.3947 | 10 | 12.92
| 7 | 2.2778 | 1.445 | 2.078 | 2.899 | 1.375 | 2.28 | 1.385 | 1.5722 | 0 | 0.018134 | 1.6344 | 0.79633 | 0 | 0 | 0.012 | 0 | -0.069 | -0.106 | 0 | -0.10082 | -0.43216 | -0.4652 | 10 | 12.47
| 8 | 2.1196 | 3.844 | 1.966 | 2.693 | 1.238 | 2.121 | 1.243 | 1.5519 | 2.4441 | 0.047822 | 1.6091 | 0.76451 | 0 | 0 | 0 | 0 | -0.457 | -0.331 | 0 | -0.18766 | -0.56288 | -0.5517 | 20 | 20
| 9 | 1.2032 | 2.167 | 1.334 | 1.593 | 0.416 | 1.204 | 0.42 | 1.1996 | 1.9321 | 0 | 1.2523 | 0.41712 | 0 | 0 | 0 | 0 | -0.861 | -0.603 | -0.11228 | -0.30235 | -0.73174 | -0.6662 | 20 | 20
| 10 | 0 | 0.159 | 0.264 | 0 | 0 | -0.399 | -1.046 | 0.58712 | 1.2397 | 0 | 0.63558 | -0.16807 | -0.0988 | 0 | -0.047 | -0.168 | -1.365 | -0.989 | -0.36477 | -0.4882 | -0.97482 | -0.8518 | 20 | 20
| 11 | -0.3574 | 0 | 0 | -0.306 | -1.145 | -2.012 | -2.585 | 0 | 0.51559 | 0 | -0.03353 | -0.79694 | -1.022 | -0.775 | -1.187 | -0.86 | -1.979 | -1.499 | -0.66069 | -0.72195 | -1.2648 | -1.0853 | 26.64 | 20
| 12 | -2.2142 | -1.927 | -0.147 | -2.277 | -2.926 | -3.385 | -3.941 | 0 | 0 | 0 | -0.67357 | -1.3983 | -1.7729 | -1.407 | -2.107 | -1.497 | -2.56 | -2.03 | -0.94273 | -0.9537 | -1.5421 | -1.3168 | 27 | 20.54
| 13 | -3.4723 | -3.305 | -1.232 | -3.608 | -4.197 | -4.382 | -4.962 | 0 | 0 | -0.5694 | -1.2303 | -1.9247 | -2.3147 | -1.85 | -2.761 | -2.001 | -3.004 | -2.469 | -1.1934 | -1.1675 | -1.7885 | -1.5304 | 27 | 22.49
| 14 | -4.0214 | -3.923 | -1.705 | -4.154 | -4.805 | -4.783 | -5.418 | 0 | 0 | -0.92744 | -1.5163 | -2.1968 | -2.5989 | -2.099 | -3.092 | -2.264 | -3.231 | -2.692 | -1.3604 | -1.3074 | -1.9516 | -1.6701 | 27 | 23.74
| 15 | -4.0239 | -3.966 | -1.796 | -4.118 | -4.909 | -4.698 | -5.427 | 0 | 0 | -1.173 | -1.6801 | -2.3715 | -2.594 | -2.135 | -3.061 | -2.242 | -3.192 | -2.645 | -1.413 | -1.3421 | -2.0008 | -1.7047 | 27 | 24.64
| 16 | -3.4753 | -3.441 | -1.52 | -3.498 | -4.446 | -4.099 | -4.905 | 0 | 0 | -1.2114 | -1.6411 | -2.3468 | -2.3269 | -1.953 | -2.681 | -1.981 | -2.905 | -2.368 | -1.3583 | -1.2783 | -1.9428 | -1.6406 | 27 | 24.91
| 17 | -2.3221 | -2.302 | -0.843 | -2.216 | -3.389 | -2.915 | -3.811 | 0 | 0 | -1.0054 | -1.3568 | -2.0834 | -1.9515 | -1.664 | -2.156 | -1.642 | -2.518 | -2.019 | -1.2639 | -1.1854 | -1.8455 | -1.5477 | 27 | 24.35
| 18 | -0.6489 | -0.637 | 0 | -0.314 | -1.841 | -1.224 | -2.24 | 0 | 0 | -0.56114 | -0.83413 | -1.5865 | -1.5665 | -1.354 | -1.647 | -1.311 | -2.126 | -1.681 | -1.1433 | -1.0758 | -1.7221 | -1.4379 | 27 | 22.94
| 19 | 0 | 0 | 0 | 0 | -0.479 | 0.257 | -0.863 | 0 | 0 | -0.19504 | -0.3958 | -1.1719 | -1.1763 | -1.034 | -1.164 | -1.003 | -1.731 | -1.37 | -1.0072 | -0.96104 | -1.5836 | -1.3231 | 23.73 | 21.65
| 20 | 0.1486 | 0.155 | 0.486 | 0.909 | 0 | 1.116 | -0.003 | 0 | 0 | 0 | -0.11193 | -0.90379 | -0.7328 | -0.657 | -0.649 | -0.694 | -1.285 | -1.058 | -0.84822 | -0.82628 | -1.4224 | -1.1882 | 20 | 20.76
| 21 | 1.0979 | 1.102 | 1.198 | 1.818 | 0 | 1.645 | 0.556 | 0 | 0.01799 | 0 | 0.13546 | -0.6734 | -0.2983 | -0.275 | -0.157 | -0.415 | -0.849 | -0.778 | -0.70104 | -0.70182 | -1.2731 | -1.0637 | 20 | 20
| 22 | 1.6738 | 1.676 | 1.641 | 2.378 | 0 | 1.993 | 0.926 | 0 | 0.26925 | 0 | 0.36388 | -0.46555 | -0.0186 | -0.028 | 0 | -0.215 | -0.569 | -0.577 | -0.59136 | -0.61213 | -1.1615 | -0.9739 | 20 | 20
| 23 | 2.0148 | 2.016 | 1.904 | 2.707 | 0.516 | 2.203 | 1.153 | 0.040877 | 0.46845 | 0 | 0.55162 | -0.2987 | 0 | 0 | 0 | -0.064 | -0.383 | -0.425 | -0.48628 | -0.52449 | -1.0547 | -0.8862 | 20 | 20
| 24 | 2.1963 | 0 | 2.043 | 2.874 | 0.89 | 2.307 | 1.283 | 0.24467 | 0 | 0 | 0.70288 | -0.16436 | 0 | 0 | 0 | 0 | -0.228 | -0.297 | -0.37086 | -0.42934 | -0.93767 | -0.791 | 11.34 | 18.01
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 4.4672 | 11.7017 | 19.6725 | 20.9717 | 16.0238 | 24.2654
| 2 | 2.8568 | 11.245 | 18.88 | 20.4879 | 14.3021 | 23.841
| 3 | 1.4091 | 10.7932 | 17.7669 | 19.6293 | 12.6782 | 23.4157
| 4 | -0.016476 | 10.3008 | 16.6508 | 18.7479 | 11.0975 | 22.967
| 5 | -1.2245 | 9.9029 | 15.4711 | 17.7906 | 9.689 | 22.6075
| 6 | -2.2862 | 9.4738 | 17.1247 | 19.3484 | 8.334 | 22.1993
| 7 | -3.193 | 9.0975 | 19.397 | 21.0886 | 7.1316 | 21.8506
| 8 | -3.3337 | 8.9582 | 20.5125 | 23.1543 | 6.5882 | 21.7274
| 9 | -0.19628 | 9.8876 | 22.8099 | 23.8657 | 8.9979 | 22.6222
| 10 | 6.8013 | 11.7551 | 25.8855 | 24.7959 | 15.0347 | 24.3831
| 11 | 15.6352 | 13.9547 | 29.838 | 25.9168 | 23.1553 | 26.4423
| 12 | 25.0661 | 16.2133 | 34.1747 | 27.0556 | 32.2721 | 28.5594
| 13 | 34.0622 | 18.3357 | 38.3724 | 28.1472 | 41.4162 | 30.5625
| 14 | 41.1697 | 19.6982 | 41.8987 | 29.0149 | 49.1534 | 31.8566
| 15 | 46.07 | 20.6912 | 44.2829 | 29.5372 | 55.1901 | 32.861
| 16 | 48.1263 | 21.0435 | 45.2962 | 29.7074 | 58.6456 | 33.2429
| 17 | 46.582 | 20.5729 | 45.2885 | 29.7175 | 58.7506 | 32.828
| 18 | 41.232 | 19.2453 | 44.6098 | 29.6094 | 55.2721 | 31.5769
| 19 | 34.5581 | 18.0354 | 33.257 | 28.4499 | 50.4057 | 30.4417
| 20 | 28.7453 | 17.2201 | 30.0661 | 26.9749 | 45.8603 | 29.6795
| 21 | 23.5942 | 16.476 | 27.4122 | 25.7654 | 41.5737 | 28.995
| 22 | 18.976 | 15.7483 | 25.8257 | 25.2338 | 37.5376 | 28.3418
| 23 | 14.9392 | 15.107 | 24.2308 | 24.4091 | 33.8308 | 27.7806
| 24 | 11.505 | 14.5494 | 22.4527 | 23.2527 | 30.4633 | 27.2948
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 0
| 1 | 3
| 2 | 8
| 3 | 19
| 4 | 32
| 5 | 31
| 6 | 42
| 7 | 60
| 8 | 110
| 9 | 95
| 10 | 112
| 11 | 155
| 12 | 190
| 13 | 230
| 14 | 229
| 15 | 244
| 16 | 291
| 17 | 297
| 18 | 334
| 19 | 337
| 20 | 313
| 21 | 324
| 22 | 267
| 23 | 253
| 24 | 252
| 25 | 241
| 26 | 254
| 27 | 241
| 28 | 264
| 29 | 297
| 30 | 298
| 31 | 331
| 32 | 377
| 33 | 384
| 34 | 411
| 35 | 363
| 36 | 315
| 37 | 255
| 38 | 208
| 39 | 132
| 40 | 75
| 41 | 45
| 42 | 24
| 43 | 12
| 44 | 5
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## EnergyPlus
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
[Note to Participants: Editorial changes: went with Hour 8 as example and 0n00 format (pertinent to Jan2018 discussion re Case 640)]
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracikng colors are:
Red is for edits from June 2013 through September 2017 distribution for the Round 3 sim trial draft.
Blue is for edits since Sep 2017 (since Sec5-2Aout-082917.xlsx):
editorial (not substantive) clarification re "hourly integrated".
| Software: | EnergyPlus | EnergyPlus
| Version: |  | Version 9.0.1
| Date of Results: |  | 2018-10-19
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.3244 | 6.027 | 3.2044 | Dec | 31 | 24 | 6.3516 | Jan | 22 | 14
| 610 | 4.3748 | 4.3328 | 3.1918 | Dec | 31 | 24 | 6.1345 | Dec | 1 | 14
| 620 | 4.4851 | 4.0595 | 3.2291 | Dec | 31 | 24 | 4.7974 | Jun | 26 | 17
| 630 | 4.7835 | 2.836 | 3.2066 | Dec | 31 | 24 | 4.2122 | Jun | 26 | 17
| 640 | 2.6618 | 5.7631 | 4.5585 | Nov | 26 | 8 | 6.2974 | Jan | 22 | 14
| 650 | 0 | 4.8168 | 0 | Jan | 1 | 1 | 6.1381 | Oct | 18 | 14
| 660 | 3.7067 | 3.2315 | 2.8311 | Dec | 31 | 24 | 3.7703 | Oct | 18 | 14
| 670 | 5.6161 | 6.6227 | 3.8535 | Nov | 26 | 7 | 6.8062 | Jan | 22 | 14
| 680 | 2.1797 | 6.4439 | 2.0524 | Nov | 26 | 7 | 6.7702 | Jan | 22 | 14
| 685 | 4.8771 | 9.1188 | 3.2232 | Dec | 31 | 24 | 7.1068 | Jan | 22 | 14
| 695 | 2.8019 | 9.1716 | 2.0718 | Dec | 31 | 24 | 7.3343 | Jan | 22 | 14
| 900 | 1.6637 | 2.4887 | 2.6875 | Feb | 9 | 6 | 3.0404 | Oct | 1 | 14
| 910 | 1.9557 | 1.3835 | 2.6989 | Feb | 9 | 6 | 2.2221 | Oct | 18 | 15
| 920 | 3.3365 | 2.7308 | 2.7702 | Feb | 9 | 6 | 3.2603 | Jun | 26 | 18
| 930 | 3.9938 | 1.9191 | 2.7849 | Feb | 9 | 6 | 2.7815 | Jun | 26 | 18
| 940 | 1.0674 | 2.4244 | 3.1428 | Dec | 31 | 9 | 3.04 | Oct | 1 | 14
| 950 | 0 | 0.70692 | 0 | Jan | 1 | 1 | 2.3875 | Sep | 11 | 15
| 960 | 2.689 | 0.90712 | 2.2594 | Feb | 9 | 6 | 1.4799 | Jun | 26 | 17
| 980 | 0.41094 | 3.7118 | 1.5378 | Feb | 9 | 6 | 3.4501 | Oct | 18 | 15
| 985 | 2.3693 | 6.3592 | 2.6954 | Feb | 9 | 6 | 3.9148 | Oct | 18 | 15
| 995 | 1.0065 | 7.2029 | 1.6221 | Feb | 9 | 6 | 4.1774 | Jan | 22 | 15
| 195 | 4.0696 | 0.61152 | 1.7944 | Dec | 31 | 24 | 1.041 | Jun | 26 | 17
| 200 | 5.1054 | 0.81408 | 2.3413 | Nov | 26 | 8 | 1.3075 | Jun | 26 | 17
| 210 | 6.0466 | 0.5599 | 2.5646 | Dec | 31 | 24 | 1.0844 | Jun | 26 | 17
| 215 | 5.4054 | 0.87747 | 2.4778 | Nov | 26 | 8 | 1.4004 | Jun | 26 | 17
| 220 | 6.4551 | 0.6099 | 2.692 | Dec | 31 | 24 | 1.1845 | Jun | 26 | 18
| 230 | 9.9299 | 0.99121 | 4.3161 | Dec | 31 | 24 | 1.8409 | Jun | 26 | 17
| 240 | 5.2794 | 0.97875 | 2.5071 | Dec | 31 | 24 | 1.3659 | Jun | 26 | 18
| 250 | 4.8991 | 3.1816 | 2.6874 | Dec | 31 | 24 | 2.8666 | Sep | 12 | 14
| 270 | 4.3854 | 7.5215 | 2.5966 | Dec | 31 | 24 | 6.8388 | Jan | 22 | 14
| 280 | 4.5701 | 5.1829 | 2.602 | Dec | 31 | 24 | 4.7272 | Jan | 22 | 14
| 290 | 4.4244 | 5.7425 | 2.5834 | Dec | 31 | 24 | 6.5946 | Jan | 22 | 14
| 300 | 4.4245 | 5.152 | 2.6031 | Dec | 31 | 24 | 4.4755 | Jun | 26 | 17
| 310 | 4.6912 | 3.6695 | 2.5801 | Dec | 31 | 24 | 3.9695 | Jun | 26 | 18
| 320 | 3.7712 | 4.986 | 2.5735 | Dec | 31 | 24 | 6.2091 | Jan | 22 | 14
| 395 | 4.6412 | 0.01038 | 1.9517 | Dec | 31 | 24 | 0.37747 | Jun | 26 | 19
| 400 | 6.3478 | 0.030566 | 2.692 | Dec | 31 | 24 | 0.60691 | Jun | 26 | 18
| 410 | 8.0803 | 0.057269 | 3.504 | Dec | 31 | 24 | 0.82785 | Jun | 26 | 18
| 420 | 6.9058 | 0.15257 | 3.3191 | Dec | 31 | 24 | 1.0325 | Jun | 26 | 18
| 430 | 5.6201 | 0.85562 | 3.3163 | Dec | 31 | 24 | 1.9294 | Jun | 26 | 16
| 440 | 4.5001 | 4.085 | 3.2187 | Dec | 31 | 24 | 4.686 | Oct | 18 | 14
| 450 | 3.9625 | 6.5073 | 3.0998 | Dec | 31 | 24 | 6.4663 | Jan | 22 | 14
| 460 | 4.1938 | 6.4746 | 3.0911 | Dec | 31 | 24 | 6.3742 | Jan | 22 | 14
| 470 | 4.0939 | 6.0294 | 3.2067 | Dec | 31 | 24 | 6.4436 | Jan | 22 | 14
| 800 | 5.1156 | 0.37353 | 2.9237 | Feb | 9 | 6 | 1.0458 | Jun | 26 | 16
| 810 | 2.3418 | 1.5078 | 2.749 | Feb | 9 | 6 | 2.2702 | Sep | 11 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 24.9173 | -12.5613 | Feb | 9 | 7 | 63.8408 | Oct | 18 | 16
| 900FF | 25.1213 | 1.2424 | Feb | 9 | 7 | 44.2922 | Sep | 12 | 15
| 650FF | 18.4195 | -17.0758 | Dec | 31 | 24 | 62.469 | Oct | 18 | 16
| 950FF | 14.789 | -12.8122 | Feb | 9 | 7 | 36.6805 | Sep | 11 | 16
| 680FF | 30.9584 | -7.0523 | Feb | 9 | 7 | 70.1447 | Jan | 22 | 16
| 980FF | 31.1618 | 9.917 | Nov | 4 | 7 | 49.6221 | Sep | 12 | 16
| 960 | 27.7427 | 5.0931 | Feb | 9 | 7 | 49.8773 | Oct | 12 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1664.3425
| NORTH | 438.241
| EAST | 1062.1572
| SOUTH | 1370.4819
| WEST | 967.278
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 804.0205
| 660/South | 435.995
| 670/South | 1024.2026
| 620/West | 581.0395
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 646.1319
| 630/West | 419.3545
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour | [15 empty] | min date | max date
| 600 | -2.0216 | -37.9798 | Dec | 31 | 24 | 24.7268 | Aug | 4 | 16 | [15 empty] | 12/31 24:00:00 | 08/04 16:00:00
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900 | [12 empty] | Case 600 |  |  |  | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling | [10 empty] | Peak Heat |  | Peak Cooling |  | Peak Heat | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour | [8 empty] | date |  |  | date | date |  | date
| Jan | 711.8797 | 521.798 | 2.9776 | 1 | 3 | 6.3516 | 22 | 14 | 255.8355 | 53.2805 | 1.9028 | 29 | 7 | 2.0779 | 22 | 15 | [8 empty] | 01/01 03:00:00 |  |  | 01/22 14:00:00 | 01/29 07:00:00 |  | 01/22 15:00:00
| Feb | 682.632 | 387.4981 | 3.0666 | 9 | 6 | 5.5373 | 2 | 14 | 294.1814 | 12.3391 | 2.6875 | 9 | 6 | 0.97943 | 15 | 15 | [8 empty] | 02/09 06:00:00 |  |  | 02/02 14:00:00 | 02/09 06:00:00 |  | 02/15 15:00:00
| Mar | 472.2167 | 484.3611 | 2.1146 | 17 | 6 | 5.0085 | 9 | 14 | 125.5424 | 65.3862 | 1.7443 | 17 | 6 | 1.4931 | 11 | 14 | [8 empty] | 03/17 06:00:00 |  |  | 03/09 14:00:00 | 03/17 06:00:00 |  | 03/11 14:00:00
| Apr | 510.1244 | 240.4611 | 2.3223 | 11 | 5 | 3.9307 | 12 | 14 | 268.6543 | 18.4694 | 2.0036 | 3 | 4 | 0.95262 | 7 | 15 | [8 empty] | 04/11 05:00:00 |  |  | 04/12 14:00:00 | 04/03 04:00:00 |  | 04/07 15:00:00
| May | 136.8192 | 339.9139 | 1.6241 | 1 | 5 | 3.0864 | 10 | 13 | 33.4139 | 114.4874 | 1.2682 | 1 | 5 | 1.5339 | 11 | 14 | [8 empty] | 05/01 05:00:00 |  |  | 05/10 13:00:00 | 05/01 05:00:00 |  | 05/11 14:00:00
| Jun | 10.0812 | 539.605 | 0.73243 | 9 | 5 | 3.4487 | 13 | 13 | 0 | 401.3344 | 0 | 1 | 1 | 1.9656 | 14 | 14 | [8 empty] | 06/09 05:00:00 |  |  | 06/13 13:00:00 | 06/01 01:00:00 |  | 06/14 14:00:00
| Jul | 12.0182 | 536.3834 | 0.51445 | 26 | 5 | 3.6284 | 17 | 14 | 0 | 398.7064 | 0 | 1 | 1 | 2.0681 | 17 | 15 | [8 empty] | 07/26 05:00:00 |  |  | 07/17 14:00:00 | 07/01 01:00:00 |  | 07/17 15:00:00
| Aug | 6.5877 | 648.5013 | 0.47852 | 17 | 6 | 4.672 | 26 | 14 | 0 | 510.3174 | 0 | 1 | 1 | 2.5258 | 29 | 15 | [8 empty] | 08/17 06:00:00 |  |  | 08/26 14:00:00 | 08/01 01:00:00 |  | 08/29 15:00:00
| Sep | 73.317 | 733.708 | 1.1295 | 28 | 24 | 5.7148 | 30 | 13 | 0.11241 | 492.837 | 0.064157 | 29 | 7 | 2.9888 | 11 | 15 | [8 empty] | 09/28 24:00:00 |  |  | 09/30 13:00:00 | 09/29 07:00:00 |  | 09/11 15:00:00
| Oct | 347.7084 | 675.2687 | 1.682 | 15 | 5 | 6.2221 | 18 | 14 | 81.0905 | 292.6655 | 1.3258 | 7 | 7 | 3.0404 | 1 | 14 | [8 empty] | 10/15 05:00:00 |  |  | 10/18 14:00:00 | 10/07 07:00:00 |  | 10/01 14:00:00
| Nov | 625.2596 | 437.6814 | 3.1061 | 26 | 7 | 6.194 | 28 | 13 | 296.9874 | 67.9828 | 2.3161 | 26 | 7 | 2.0018 | 20 | 15 | [8 empty] | 11/26 07:00:00 |  |  | 11/28 13:00:00 | 11/26 07:00:00 |  | 11/20 15:00:00
| Dec | 735.7303 | 481.8594 | 3.2044 | 31 | 24 | 6.251 | 1 | 14 | 307.8688 | 60.9353 | 2.1749 | 31 | 7 | 1.9682 | 2 | 15 | [8 empty] | 12/31 24:00:00 |  |  | 12/01 14:00:00 | 12/31 07:00:00 |  | 12/02 15:00:00
| Total | 4324.3743 | 6027.0394 | [6 empty] | 1663.6867 | 2488.7414
| Max |  |  | 3.2044 |  |  | 6.3516 |  |  |  |  | 2.6875 |  |  | 3.0404
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -22.9659 | -1.17 | 4.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -24.1358 | -1.1879 | 3.8578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -25.3162 | -1.261 | 2.9526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -27.1947 | -1.4438 | 1.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 5.6503 | 2.825 | 2.825 | -26.8988 | -1.4438 | 0.74467 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6849 | 0.91674 | 2.1275
| 6 | 21.25 | 10.9831 | 10.9831 | 103.1926 | 27.0562 | 27.0562 | -26.6742 | -1.4438 | 1.7866 | 0 | 0 | 0 | 6.5505 | 3.5641 | 8.271 | 16.1367 | 8.7799 | 20.3752
| 7 | 64.75 | 33.8229 | 33.8229 | 289.8646 | 55.3885 | 55.3885 | -27.3883 | -1.1879 | 4.4173 | 0 | 0 | 0 | 20.1724 | 10.9757 | 25.471 | 33.0345 | 17.9739 | 41.7114
| 8 | 114.5833 | 59.9654 | 59.7762 | 493.4291 | 82.404 | 81.9746 | -26.6041 | -0.87772 | 6.596 | 109.5631 | 58.7036 | 144.9621 | 35.7642 | 19.4591 | 45.1581 | 48.9027 | 26.6079 | 61.7496
| 9 | 160.25 | 84.3926 | 83.0745 | 682.3352 | 179.1211 | 104.1185 | -25.3596 | -0.53267 | 8.3915 | 323.8 | 175.1923 | 408.8652 | 50.3329 | 27.3858 | 63.5536 | 70.5019 | 38.6289 | 96.4962
| 10 | 203.25 | 108.1146 | 104.629 | 837.8445 | 305.7869 | 119.4839 | -24.4946 | 0.6528 | 10.7117 | 484.0809 | 263.0242 | 596.1031 | 64.481 | 35.0837 | 81.4178 | 116.644 | 63.0283 | 170.6848
| 11 | 259.8333 | 139.6057 | 132.0397 | 947.9972 | 396.7139 | 128.2458 | -23.1465 | 1.865 | 12.6113 | 591.9351 | 322.5677 | 720.937 | 83.2627 | 45.3028 | 105.1329 | 169.4457 | 90.4757 | 244.3135
| 12 | 276.5833 | 149.4359 | 140.236 | 1005.2373 | 443.5116 | 131.5461 | -21.7912 | 2.0953 | 13.2726 | 648.7354 | 354.5078 | 786.606 | 89.1256 | 48.4927 | 112.5357 | 201.8158 | 107.4787 | 286.2069
| 13 | 274.0833 | 147.9223 | 142.6342 | 1004.0328 | 442.6572 | 258.9316 | -20.2132 | 0.88422 | 13.895 | 654.8384 | 357.9765 | 793.6699 | 88.2229 | 48.0015 | 111.3958 | 201.2382 | 107.1723 | 285.4691
| 14 | 255.1667 | 136.7123 | 137.7338 | 946.1468 | 394.8902 | 491.6517 | -20.6931 | -0.55214 | 14.3919 | 609.2696 | 332.2657 | 740.9315 | 81.5371 | 44.3638 | 102.9539 | 168.1713 | 89.8075 | 242.6571
| 15 | 222 | 117.6082 | 123.3077 | 835.4779 | 303.1678 | 683.8576 | -21.7664 | -2.0361 | 14.9 | 513.0433 | 278.943 | 629.5384 | 70.1431 | 38.1645 | 88.5672 | 115.2723 | 62.3178 | 168.6678
| 16 | 172 | 90.0007 | 96.8707 | 679.2595 | 175.5288 | 811.9781 | -22.2074 | -1.9974 | 14.7769 | 366.6641 | 198.6673 | 459.3639 | 53.6776 | 29.2057 | 67.7768 | 69.6148 | 38.1416 | 94.9682
| 17 | 101.9167 | 53.2617 | 54.9349 | 489.9716 | 81.5142 | 853.4406 | -22.932 | -1.8299 | 14.4692 | 178.3747 | 95.7857 | 233.5125 | 31.766 | 17.2837 | 40.1098 | 48.6162 | 26.4518 | 61.3859
| 18 | 50.25 | 26.165 | 26.165 | 285.8351 | 54.8088 | 778.077 | -24.6208 | -2.1057 | 13.5976 | 9.7889 | 5.1964 | 13.5578 | 15.6051 | 8.4907 | 19.704 | 32.6887 | 17.7857 | 41.2749
| 19 | 10.5278 | 5.4293 | 5.4293 | 99.0838 | 26.2621 | 527.4004 | -25.9163 | -2.3646 | 12.3123 | 0 | 0 | 0 | 3.2381 | 1.7618 | 4.0886 | 15.6631 | 8.5222 | 19.7772
| 20 | 0 | 0 | 0 | 4.4364 | 2.3496 | 70.2141 | -26.5019 | -2.9405 | 11.5045 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4014 | 0.76247 | 1.7694
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -27.6142 | -3.2197 | 9.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -28.9393 | -3.7455 | 7.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -29.4433 | -4.7857 | 7.1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -29.2659 | -5.2605 | 5.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.1523 | 0.082706 | 1.8505 | 2.6246 | 1.2516 | 2.1861 | 1.384 | 0.97734 | 0 | 0 | 1.1316 | 0.50876 | 0 | 0 | 0 | 0 | -0.084479 | -0.15693 | -0.10115 | -0.21575 | -0.71075 | -0.64079 | 10.7291 | 15.6174
| 2 | 2.2223 | 0.54755 | 1.9038 | 2.7315 | 1.3644 | 2.2406 | 1.4443 | 1.0829 | 0 | 0 | 1.2332 | 0.59729 | 0 | 0 | 0 | 0 | -0.025064 | -0.10057 | -0.030142 | -0.15588 | -0.62348 | -0.57552 | 10 | 15.0057
| 3 | 2.2757 | 0.91754 | 1.9434 | 2.8196 | 1.4425 | 2.2855 | 1.4903 | 1.1826 | 0 | 0 | 1.3297 | 0.67434 | 0 | 0 | 0 | 0 | 0.056452 | -0.041091 | 0 | -0.093652 | -0.52735 | -0.5033 | 10 | 14.4319
| 4 | 2.3283 | 1.1473 | 1.9828 | 2.9079 | 1.5049 | 2.3336 | 1.5334 | 1.2862 | 0 | 0.010067 | 1.4277 | 0.74589 | 0 | 0 | 0 | 0 | 0.17529 | 0.017247 | 0 | -0.024143 | -0.42151 | -0.42781 | 10 | 13.8638
| 5 | 2.351 | 1.2747 | 1.9989 | 2.9498 | 1.5323 | 2.3538 | 1.5491 | 1.366 | 0 | 0.11176 | 1.5004 | 0.78604 | 0 | 0 | 0.11574 | 0 | 0.27165 | 0.071385 | 0 | 0 | -0.32772 | -0.35439 | 10 | 13.3569
| 6 | 2.3515 | 1.3397 | 2.0006 | 2.9434 | 1.5467 | 2.353 | 1.5567 | 1.4385 | 0 | 0.22968 | 1.5653 | 0.81681 | 0 | 0 | 0.10059 | 0 | 0.16084 | 0.032137 | 0 | 0 | -0.33274 | -0.37247 | 10 | 12.884
| 7 | 2.3551 | 1.3839 | 2.0091 | 2.9242 | 1.5469 | 2.3559 | 1.5531 | 1.5049 | 0 | 0.32252 | 1.6239 | 0.8414 | 0 | 0 | 0 | 0 | -0.13512 | -0.1231 | 0 | -0.062989 | -0.44088 | -0.46548 | 10 | 12.4205
| 8 | 1.8832 | 3.3808 | 1.7123 | 2.3743 | 1.1609 | 1.8836 | 1.1644 | 1.3243 | 1.2639 | 0.19642 | 1.4296 | 0.68673 | 0 | 0 | 0 | 0 | -0.53511 | -0.38175 | -0.016529 | -0.17091 | -0.59821 | -0.57861 | 15.8147 | 15.9824
| 9 | 0.49397 | 1.7525 | 0.82326 | 0.72924 | 0.15573 | 0.46459 | -0.078065 | 0.79271 | 1.5508 | 0 | 0.87469 | 0.24592 | 0 | 0 | 0 | 0 | -1.0194 | -0.73521 | -0.15912 | -0.30246 | -0.79838 | -0.73081 | 20 | 20
| 10 | 0 | 0.053533 | 0.061784 | 0 | -0.11857 | -1.3367 | -2.0066 | 0.26716 | 0.82256 | 0 | 0.34915 | -0.3633 | -0.35948 | -0.16326 | -0.42413 | -0.32663 | -1.7043 | -1.2892 | -0.41739 | -0.52915 | -1.1091 | -0.98589 | 21.32 | 20
| 11 | -1.3089 | -0.67412 | 0 | -1.2959 | -2.26 | -3.2585 | -3.9354 | 0 | 0.29741 | 0 | -0.25363 | -1.0539 | -1.4584 | -0.88657 | -1.7545 | -1.2062 | -2.5672 | -2.0148 | -0.76505 | -0.82735 | -1.4971 | -1.3035 | 26.4903 | 20
| 12 | -3.4074 | -3.0125 | -0.49567 | -3.5295 | -4.3177 | -4.6823 | -5.3726 | 0 | 0 | -0.11102 | -0.93631 | -1.7987 | -2.4228 | -1.5988 | -2.8853 | -2.0156 | -3.316 | -2.6747 | -1.1012 | -1.0995 | -1.8618 | -1.5915 | 27 | 20.9908
| 13 | -4.6741 | -4.5085 | -1.6957 | -4.9384 | -5.523 | -5.6082 | -6.2586 | 0 | 0 | -0.74762 | -1.6478 | -2.5159 | -2.8449 | -1.9127 | -3.3784 | -2.5062 | -3.614 | -3.0711 | -1.3309 | -1.3165 | -2.1009 | -1.8176 | 27 | 23.1192
| 14 | -4.9334 | -4.868 | -2.1841 | -5.1408 | -5.7122 | -5.7135 | -6.2995 | 0 | 0 | -1.1811 | -2.0379 | -2.8801 | -2.9085 | -2.0065 | -3.4483 | -2.6048 | -3.6138 | -3.1133 | -1.4697 | -1.4417 | -2.2354 | -1.9425 | 27 | 24.6214
| 15 | -4.1722 | -4.1472 | -1.8726 | -4.1667 | -5.0803 | -4.881 | -5.6031 | -0.046329 | 0 | -1.3476 | -2.082 | -2.9303 | -2.641 | -1.9013 | -3.1098 | -2.348 | -3.3078 | -2.8203 | -1.4822 | -1.438 | -2.2319 | -1.9297 | 27 | 25.2509
| 16 | -2.9277 | -2.918 | -1.2021 | -2.7773 | -3.9171 | -3.5937 | -4.3995 | -0.027472 | 0 | -1.2768 | -1.9005 | -2.7431 | -2.2096 | -1.6894 | -2.5271 | -1.8957 | -2.8517 | -2.3445 | -1.399 | -1.33 | -2.1292 | -1.8097 | 27 | 25.2715
| 17 | -1.2391 | -1.2353 | -0.29981 | -0.98623 | -2.2347 | -1.876 | -2.7038 | 0 | 0 | -0.87926 | -1.3981 | -2.2176 | -1.7631 | -1.4112 | -1.9379 | -1.505 | -2.3954 | -1.947 | -1.291 | -1.2236 | -2.0064 | -1.6975 | 27 | 24.483
| 18 | -0.019928 | -0.019589 | 0 | 0 | -0.36295 | 0.036899 | -0.72678 | 0 | 0 | -0.21836 | -0.63216 | -1.4023 | -1.37 | -1.1343 | -1.4631 | -1.1869 | -1.9943 | -1.6239 | -1.1649 | -1.1098 | -1.8639 | -1.5763 | 25.4595 | 22.7901
| 19 | 0.086501 | 0.087045 | 0.10283 | 0.4619 | 0 | 1.1009 | 0.31916 | 0 | 0 | 0 | -0.18634 | -0.925 | -0.98285 | -0.84941 | -1.0152 | -0.87653 | -1.5926 | -1.3044 | -1.0134 | -0.96893 | -1.6925 | -1.4243 | 21.1465 | 21.4689
| 20 | 0.98137 | 0.98216 | 0.84738 | 1.6223 | 0 | 1.6905 | 0.74894 | 0 | 0 | 0 | 0.1006 | -0.60955 | -0.56694 | -0.52226 | -0.55242 | -0.57282 | -1.1479 | -0.98545 | -0.84554 | -0.81412 | -1.5015 | -1.2553 | 20 | 20.5229
| 21 | 1.6393 | 1.6398 | 1.4079 | 2.2179 | 0.26604 | 2.0307 | 1.0411 | 0 | 0.12095 | 0 | 0.33635 | -0.35944 | -0.231 | -0.24015 | -0.17822 | -0.33075 | -0.78159 | -0.73214 | -0.70239 | -0.68625 | -1.3387 | -1.116 | 20 | 20.0026
| 22 | 2.0595 | 2.0598 | 1.7785 | 2.6015 | 0.76843 | 2.2766 | 1.2788 | 0 | 0.38542 | 0 | 0.5638 | -0.13628 | -0.04743 | -0.081429 | -0.0080085 | -0.16755 | -0.5735 | -0.56394 | -0.59073 | -0.59068 | -1.2139 | -1.0144 | 20 | 20
| 23 | 2.3234 | 2.3235 | 2.0051 | 2.8785 | 1.0956 | 2.4412 | 1.4531 | 0.17522 | 0.61003 | 0 | 0.75784 | 0.056384 | 0 | -0.0055834 | 0 | -0.053704 | -0.43593 | -0.44324 | -0.48864 | -0.5056 | -1.0991 | -0.92336 | 20 | 20
| 24 | 2.4352 | 0 | 2.1 | 2.9941 | 1.3198 | 2.4984 | 1.5445 | 0.39699 | 0 | 0 | 0.89065 | 0.19471 | 0 | 0 | 0 | 0 | -0.30738 | -0.3341 | -0.37539 | -0.41088 | -0.97318 | -0.82306 | 12.9018 | 18.0038
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 5.443 | 12.938 | 19.8711 | 21.2303 | 15.3461 | 22.7451
| 2 | 3.8072 | 12.4251 | 19.0627 | 20.7155 | 13.4846 | 22.2438
| 3 | 2.3742 | 11.9298 | 18.14 | 20.0299 | 11.7774 | 21.7632
| 4 | 1.0857 | 11.432 | 17.0158 | 19.1593 | 10.1946 | 21.2816
| 5 | -0.0051534 | 10.9913 | 15.8836 | 18.2535 | 8.775 | 20.8555
| 6 | -0.89643 | 10.5804 | 16.3875 | 18.6317 | 7.5063 | 20.459
| 7 | -1.7104 | 10.1741 | 18.7611 | 20.2686 | 6.3475 | 20.0788
| 8 | -1.4759 | 10.3241 | 20.8898 | 22.8727 | 6.2878 | 20.2516
| 9 | 2.7076 | 11.7504 | 23.2971 | 24.4046 | 10.0373 | 21.6585
| 10 | 9.9288 | 13.8083 | 26.426 | 25.569 | 16.5873 | 23.5492
| 11 | 18.7293 | 15.9577 | 30.6202 | 26.9141 | 24.697 | 25.5857
| 12 | 28.01 | 18.2069 | 35.2192 | 28.1778 | 33.6544 | 27.7875
| 13 | 36.5705 | 20.4419 | 39.1876 | 29.1272 | 42.5122 | 29.9726
| 14 | 43.3942 | 22.0116 | 42.1006 | 29.8598 | 49.7746 | 31.4705
| 15 | 46.9798 | 22.7239 | 44.2085 | 30.2902 | 54.3914 | 32.0838
| 16 | 47.5927 | 22.8195 | 44.886 | 30.4309 | 56.3144 | 32.1996
| 17 | 44.8818 | 22.102 | 44.6042 | 30.4338 | 54.9811 | 31.4583
| 18 | 38.7015 | 20.4887 | 43.7421 | 30.3524 | 50.2114 | 29.8322
| 19 | 32.1639 | 19.2192 | 34.4834 | 29.0273 | 44.9265 | 28.6662
| 20 | 26.2951 | 18.324 | 30.8554 | 27.6463 | 39.9705 | 27.8593
| 21 | 21.5268 | 17.5351 | 27.9576 | 26.3384 | 35.6029 | 27.1608
| 22 | 17.0314 | 16.7569 | 25.9916 | 25.5339 | 31.6493 | 26.4922
| 23 | 13.2781 | 15.9944 | 24.5462 | 24.8642 | 28.034 | 25.8183
| 24 | 10.2079 | 15.3612 | 22.9825 | 23.8852 | 24.8425 | 25.2512
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 0
| 1 | 4
| 2 | 4
| 3 | 20
| 4 | 21
| 5 | 39
| 6 | 51
| 7 | 63
| 8 | 71
| 9 | 83
| 10 | 128
| 11 | 164
| 12 | 218
| 13 | 185
| 14 | 197
| 15 | 253
| 16 | 269
| 17 | 241
| 18 | 312
| 19 | 321
| 20 | 337
| 21 | 305
| 22 | 324
| 23 | 302
| 24 | 276
| 25 | 296
| 26 | 283
| 27 | 313
| 28 | 302
| 29 | 326
| 30 | 356
| 31 | 386
| 32 | 366
| 33 | 399
| 34 | 374
| 35 | 315
| 36 | 253
| 37 | 209
| 38 | 152
| 39 | 118
| 40 | 64
| 41 | 34
| 42 | 17
| 43 | 7
| 44 | 2
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760
Intermediate calculation cells
DATE
02/11
02/11
02/07
02/11
02/11
02/11
02/11
DATE
07/20
04/23
04/29
10/06
10/06
10/06
10/06
DATE
11/26
12/31
01/22
10/18
01/22
10/18
01/15
DATE
06/27
06/17
07/11
06/02
05/10
09/17
08/01

## ESP-r
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracking colors are:
Red is for edits from June 2013 through April 2018 distribution for the Round 3 sim trial draft.
| Software: | ESP-r
| Version: | 13.3
| Date of Results: |  | 26th April 2019
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.362 | 6.1618 | 3.228 | Jan | 1 | 1 | 6.193 | Jan | 22 | 14
| 610 | 4.527 | 4.2325 | 3.233 | Jan | 1 | 1 | 5.934 | Jan | 22 | 14
| 620 | 4.5143 | 4.2457 | 3.253 | Jan | 1 | 1 | 4.622 | Jun | 26 | 17
| 630 | 5.0506 | 2.5953 | 3.259 | Jan | 1 | 1 | 3.971 | Jun | 26 | 17
| 640 | 2.6544 | 5.8926 | 4.101 | Nov | 26 | 8 | 6.127 | Jan | 22 | 14
| 650 | 0 | 4.9451 | 0 | Jan | 1 | 1 | 5.961 | Oct | 18 | 14
| 660 | 3.787 | 3.2186 | 2.846 | Jan | 1 | 1 | 3.53 | Oct | 1 | 14
| 670 | 5.975 | 6.5203 | 3.992 | Nov | 26 | 7 | 6.482 | Oct | 18 | 14
| 680 | 2.1321 | 6.5294 | 2.022 | Feb | 9 | 7 | 6.676 | Jan | 22 | 14
| 685 | 4.9035 | 9.1214 | 3.247 | Jan | 1 | 1 | 6.934 | Jan | 22 | 14
| 695 | 2.7321 | 9.149 | 2.025 | Nov | 26 | 7 | 7.239 | Jan | 22 | 14
| 900 | 1.5847 | 2.4877 | 2.633 | Feb | 9 | 7 | 2.896 | Oct | 12 | 15
| 910 | 2.0672 | 1.2829 | 2.684 | Feb | 9 | 7 | 2.212 | Oct | 2 | 15
| 920 | 3.2997 | 2.8144 | 2.706 | Feb | 9 | 7 | 3.099 | Jun | 26 | 18
| 930 | 4.2776 | 1.6538 | 2.765 | Feb | 9 | 6 | 2.494 | Jun | 26 | 18
| 940 | 1.0147 | 2.4276 | 3.122 | Feb | 9 | 9 | 2.891 | Oct | 12 | 15
| 950 | 0 | 0.656 | 0 | Jan | 1 | 1 | 2.202 | Sep | 10 | 15
| 960 | 2.6239 | 0.9496 | 2.201 | Feb | 9 | 6 | 1.403 | Jun | 26 | 17
| 980 | 0.3511 | 3.7745 | 1.473 | Feb | 9 | 7 | 3.341 | Oct | 12 | 15
| 985 | 2.2833 | 6.2493 | 2.642 | Feb | 9 | 7 | 3.736 | Oct | 12 | 15
| 995 | 0.9048 | 7.1488 | 1.56 | Feb | 9 | 7 | 3.954 | Jan | 22 | 15
| 195 | 3.9509 | 0.611 | 1.802 | Jan | 1 | 1 | 0.944 | Jun | 26 | 17
| 200 | 4.9204 | 0.8004 | 2.275 | Dec | 31 | 24 | 1.198 | Jun | 26 | 17
| 210 | 6.3171 | 0.5185 | 2.671 | Jan | 1 | 1 | 0.877 | Jun | 14 | 14
| 215 | 5.1811 | 0.8948 | 2.39 | Nov | 26 | 8 | 1.366 | Jun | 26 | 17
| 220 | 6.7257 | 0.5762 | 2.788 | Jan | 1 | 1 | 1.012 | Jun | 14 | 15
| 230 | 9.9385 | 0.955 | 4.16 | Jan | 1 | 1 | 1.701 | Jun | 26 | 17
| 240 | 5.5393 | 0.9218 | 2.605 | Jan | 1 | 1 | 1.192 | Jun | 14 | 15
| 250 | 4.935 | 3.4668 | 2.78 | Jan | 1 | 1 | 3.034 | Sept | 12 | 14
| 270 | 4.5764 | 7.3086 | 2.748 | Jan | 1 | 1 | 6.613 | Jan | 22 | 14
| 280 | 4.7381 | 5.2058 | 2.752 | Jan | 1 | 1 | 4.676 | Jan | 22 | 14
| 290 | 4.7447 | 5.3206 | 2.75 | Jan | 1 | 1 | 6.411 | Jan | 22 | 14
| 300 | 4.6679 | 5.0381 | 2.766 | Jan | 1 | 1 | 4.221 | Jun | 26 | 17
| 310 | 5.2396 | 3.1279 | 2.771 | Jan | 1 | 1 | 3.618 | Jun | 26 | 18
| 320 | 3.9699 | 4.9131 | 2.733 | Jan | 1 | 2 | 5.993 | Jan | 22 | 14
| 395 | 4.8657 | 0.0055 | 2.09 | Jan | 1 | 2 | 0.294 | Aug | 5 | 18
| 400 | 6.61 | 0.0244 | 2.788 | Jan | 1 | 1 | 0.456 | Aug | 5 | 17
| 410 | 8.2122 | 0.0523 | 3.473 | Jan | 1 | 1 | 0.624 | Jun | 26 | 18
| 420 | 7.027 | 0.1419 | 3.29 | Jan | 1 | 1 | 0.836 | Jun | 26 | 17
| 430 | 5.5449 | 0.9527 | 3.285 | Jan | 1 | 1 | 1.874 | Jul | 17 | 14
| 440 | 4.5039 | 4.4141 | 3.237 | Jan | 1 | 1 | 4.679 | Oct | 18 | 14
| 450 | 3.8503 | 6.6132 | 3.042 | Jan | 1 | 1 | 6.501 | Jan | 22 | 14
| 460 | 4.2625 | 6.7291 | 3.101 | Jan | 1 | 1 | 6.304 | Jan | 22 | 14
| 470 | 3.9597 | 6.0054 | 3.169 | Jan | 1 | 1 | 6.407 | Jan | 22 | 14
| 800 | 4.9798 | 0.3914 | 2.84 | Feb | 9 | 7 | 1.052 | Aug | 5 | 15
| 810 | 2.185 | 1.6056 | 2.695 | Feb | 9 | 7 | 2.179 | Sep | 4 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 25.26 | -13.5 | Feb | 9 | 7 | 64.6 | Oct | 1 | 16
| 900FF | 25.34 | 1.6 | Feb | 9 | 7 | 44.3 | Sep | 12 | 16
| 650FF | 18.93 | -17.5 | Jan | 1 | 1 | 63.3 | Oct | 1 | 16
| 950FF | 14.78 | -12.5 | Feb | 9 | 6 | 36.4 | Aug | 5 | 16
| 680FF | 31.71 | -7.2 | Feb | 9 | 7 | 72.2 | Oct | 12 | 16
| 980FF | 31.84 | 10.5 | Nov | 4 | 8 | 50.2 | Sep | 12 | 15
| 960 | 27.74 | 5 | Feb | 9 | 7 | 49.5 | Oct | 12 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1665.18
| NORTH | 432.12
| EAST | 1054.24
| SOUTH | 1363.1
| WEST | 961.18
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 813.88
| 660/South | 442.7
| 670/South | 1028.35
| 620/West | 591.88
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 631.33
| 630/West | 389.67
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -5.17 | -46.9 | Dec | 31 | 23 | 26.7 | Aug | 4 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 732 | 523 | 3.23 | 1 | 1 | 6.19 | 22 | 14 | 266 | 42 | 2.2 | 1 | 5 | 1.81 | 22 | 16
| Feb | 682 | 398 | 3.14 | 9 | 6 | 5.42 | 2 | 14 | 283 | 11 | 2.63 | 9 | 7 | 0.85 | 15 | 16
| Mar | 481 | 489 | 2.23 | 17 | 6 | 5.04 | 9 | 14 | 115 | 56 | 1.76 | 17 | 7 | 1.27 | 10 | 15
| Apr | 479 | 263 | 2.38 | 11 | 6 | 4.04 | 12 | 14 | 228 | 22 | 1.93 | 3 | 4 | 0.95 | 8 | 15
| May | 139 | 364 | 1.75 | 1 | 5 | 3.1 | 10 | 14 | 29 | 125 | 1.23 | 1 | 5 | 1.46 | 11 | 15
| Jun | 14 | 550 | 0.76 | 10 | 5 | 3.43 | 13 | 14 | 0 | 404 | 0 | 1 | 1 | 1.89 | 14 | 15
| Jul | 14 | 556 | 0.57 | 26 | 5 | 3.64 | 17 | 14 | 0 | 410 | 0 | 1 | 1 | 1.97 | 17 | 15
| Aug | 9 | 674 | 0.56 | 17 | 6 | 4.7 | 29 | 14 | 0 | 531 | 0 | 1 | 1 | 2.51 | 29 | 15
| Sep | 81 | 743 | 1.19 | 29 | 1 | 5.58 | 30 | 14 | 0 | 492 | 0 | 1 | 1 | 2.81 | 11 | 15
| Oct | 354 | 681 | 1.77 | 9 | 6 | 6.07 | 18 | 14 | 70 | 281 | 1.21 | 7 | 7 | 2.9 | 12 | 15
| Nov | 629 | 444 | 3.11 | 26 | 7 | 6.03 | 28 | 14 | 286 | 63 | 2.28 | 26 | 8 | 1.94 | 20 | 15
| Dec | 750 | 476 | 3.17 | 31 | 24 | 6.12 | 1 | 14 | 308 | 48 | 2.04 | 9 | 7 | 1.67 | 2 | 15
| Total | 4364 | 6161 | [6 empty] | 1585 | 2485
| Max |  |  | 3.23 |  |  | 6.19 |  |  |  |  | 2.63 |  |  | 2.9
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -30.02 | 0.09 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -27.59 | 0.67 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -34.17 | 0.04 | -1.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -37.85 | -0.01 | -2.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 2.88 | 1.27 | 1.27 | -35.32 | -0.06 | -4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.44 | 1
| 6 | 17.81 | 9.22 | 9.22 | 90.78 | 24.28 | 24.28 | -36.27 | -0.11 | -1.82 | 0 | 0 | 0 | 5.81 | 3.16 | 7.24 | 15.28 | 8.33 | 19.06
| 7 | 60.75 | 31.59 | 31.59 | 272.39 | 52.29 | 52.29 | -39.06 | 0.44 | 0.27 | 0 | 0 | 0 | 19.89 | 10.83 | 24.8 | 32.92 | 17.93 | 41.04
| 8 | 110.5 | 57.22 | 56.9 | 475.84 | 79.31 | 78.93 | -35.71 | 0.44 | 1.19 | 98.09 | 52.46 | 130.57 | 36.03 | 19.62 | 44.92 | 49.71 | 27.07 | 61.97
| 9 | 156.75 | 82.11 | 80.12 | 666.65 | 166.72 | 101.39 | -37.21 | 0.93 | 2.34 | 305.31 | 165.67 | 385.67 | 51.69 | 28.16 | 64.45 | 72.36 | 39.24 | 94.38
| 10 | 198.88 | 105.56 | 100.9 | 825.46 | 295.8 | 117.25 | -36.53 | 2.52 | 5.18 | 471.51 | 257.88 | 580.1 | 66.46 | 36.2 | 82.87 | 117.05 | 62.79 | 166.3
| 11 | 256.38 | 137.73 | 128.06 | 939.78 | 390.25 | 126.5 | -35.02 | 3.53 | 5.23 | 588.43 | 323.46 | 713.01 | 86.72 | 47.23 | 108.12 | 169.35 | 90.23 | 238.75
| 12 | 276 | 149.3 | 137.41 | 1001.8 | 441.16 | 130.19 | -34.15 | 3.08 | 5.13 | 646.8 | 356.29 | 781.74 | 94 | 51.2 | 117.2 | 204.8 | 108.79 | 284.99
| 13 | 274.88 | 148.6 | 141.06 | 1005.59 | 444.52 | 238.72 | -32.27 | 1.37 | 5.64 | 656.6 | 361.81 | 793.35 | 93.56 | 50.96 | 116.65 | 207.38 | 110.14 | 288.31
| 14 | 257.25 | 137.97 | 138.78 | 952.44 | 400.86 | 471.42 | -33.6 | 0.32 | 4.83 | 617.5 | 339.8 | 747 | 86.87 | 47.31 | 108.31 | 176.25 | 93.84 | 247.87
| 15 | 225.25 | 119.2 | 126.87 | 846.07 | 312.83 | 668.03 | -33.59 | -1.39 | 6.27 | 523.9 | 287.23 | 639.47 | 75.05 | 40.88 | 93.57 | 125.09 | 67.02 | 178.35
| 16 | 177.12 | 92.17 | 103.03 | 693.34 | 187.96 | 802.57 | -33.87 | -0.21 | 5.29 | 378.6 | 206.18 | 472.35 | 58.03 | 31.61 | 72.35 | 77.7 | 42.07 | 103.01
| 17 | 107.25 | 55.39 | 61.13 | 506.28 | 85.41 | 852.47 | -34.35 | -0.63 | 6.77 | 190.97 | 102.75 | 248.72 | 34.87 | 18.99 | 43.48 | 52.17 | 28.42 | 65.1
| 18 | 54.12 | 28.16 | 28.89 | 302.71 | 56.38 | 789.03 | -36.61 | -0.64 | 5.56 | 10.84 | 5.76 | 14.74 | 17.73 | 9.66 | 22.11 | 35.49 | 19.33 | 44.25
| 19 | 14.19 | 7.34 | 7.34 | 112.8 | 28.15 | 555.16 | -36.72 | -1.12 | 5.12 | 0 | 0 | 0 | 4.62 | 2.52 | 5.76 | 17.72 | 9.65 | 22.1
| 20 | 0 | 0 | 0 | 7.48 | 3.31 | 94.52 | -37.14 | -1.62 | 5.75 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 1.13 | 2.6
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -38.24 | -1.57 | 2.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -39.11 | -2.24 | 2.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -39.18 | -3.35 | 1.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.79 | -3.34 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.08 | 0.08 | 1.79 | 2.68 | 1.17 | 2.12 | 1.31 | 0.91 | 0 | 0 | 1.07 | 0.42 | 0 | 0 | 0 | 0 | -0.04 | -0.14 | -0.17 | -0.27 | -0.76 | -0.68 | 10.63 | 16.04
| 2 | 2.22 | 0.6 | 1.89 | 2.95 | 1.32 | 2.25 | 1.41 | 1.06 | 0 | 0 | 1.2 | 0.54 | 0 | 0 | 0 | 0 | 0.05 | -0.07 | -0.09 | -0.21 | -0.66 | -0.61 | 10 | 15.32
| 3 | 2.3 | 0.99 | 1.94 | 3.1 | 1.42 | 2.32 | 1.48 | 1.17 | 0 | 0 | 1.3 | 0.63 | 0 | 0 | 0 | 0 | 0.13 | -0.02 | -0.01 | -0.14 | -0.57 | -0.54 | 10 | 14.71
| 4 | 2.38 | 1.21 | 2 | 3.24 | 1.5 | 2.39 | 1.54 | 1.27 | 0 | 0 | 1.4 | 0.71 | 0 | 0 | 0.12 | 0 | 0.26 | 0.04 | 0 | -0.06 | -0.46 | -0.46 | 10 | 14.11
| 5 | 2.42 | 1.35 | 2.04 | 3.31 | 1.55 | 2.43 | 1.57 | 1.36 | 0 | 0 | 1.48 | 0.77 | 0.04 | 0 | 0.33 | 0 | 0.35 | 0.11 | 0 | -0.01 | -0.35 | -0.38 | 10 | 13.55
| 6 | 2.43 | 1.42 | 2.05 | 3.31 | 1.57 | 2.44 | 1.59 | 1.43 | 0 | 0.1 | 1.55 | 0.81 | 0.09 | 0 | 0.29 | 0 | 0.26 | 0.09 | 0 | 0 | -0.32 | -0.37 | 10 | 13.05
| 7 | 2.46 | 1.48 | 2.08 | 3.3 | 1.59 | 2.46 | 1.6 | 1.51 | 0 | 0.22 | 1.62 | 0.85 | 0 | 0 | 0.02 | 0 | -0.09 | -0.06 | 0 | -0.06 | -0.4 | -0.44 | 10 | 12.53
| 8 | 2.09 | 3.06 | 1.86 | 2.84 | 1.3 | 2.09 | 1.31 | 1.42 | 1.13 | 0.19 | 1.52 | 0.76 | 0 | 0 | 0 | 0 | -0.45 | -0.3 | 0 | -0.16 | -0.52 | -0.54 | 15 | 15.29
| 9 | 0.79 | 1.94 | 1.01 | 1.21 | 0.34 | 0.77 | 0.25 | 0.93 | 1.7 | 0.01 | 1.02 | 0.37 | 0 | 0 | 0 | 0 | -0.91 | -0.63 | -0.11 | -0.27 | -0.68 | -0.66 | 20 | 20
| 10 | 0 | 0.15 | 0.13 | 0.02 | -0.1 | -1.11 | -1.63 | 0.38 | 0.91 | 0 | 0.46 | -0.2 | -0.23 | -0.08 | -0.26 | -0.19 | -1.55 | -1.14 | -0.31 | -0.45 | -0.94 | -0.88 | 21.16 | 20
| 11 | -1.28 | -0.7 | 0 | -1.14 | -1.98 | -3.12 | -3.67 | 0.01 | 0.44 | 0 | -0.12 | -0.88 | -1.21 | -0.65 | -1.43 | -0.99 | -2.36 | -1.84 | -0.61 | -0.72 | -1.29 | -1.17 | 26.39 | 20.21
| 12 | -3.36 | -2.96 | -0.47 | -3.35 | -4.13 | -4.62 | -5.21 | 0 | 0.04 | -0.09 | -0.77 | -1.6 | -2.22 | -1.38 | -2.61 | -1.84 | -3.14 | -2.53 | -0.94 | -1 | -1.65 | -1.46 | 27 | 20.78
| 13 | -4.69 | -4.51 | -1.63 | -4.86 | -5.48 | -5.6 | -6.22 | 0 | 0 | -0.69 | -1.48 | -2.34 | -2.78 | -1.81 | -3.26 | -2.42 | -3.55 | -3 | -1.21 | -1.23 | -1.93 | -1.71 | 27 | 22.86
| 14 | -5.08 | -5 | -2.18 | -5.1 | -5.85 | -5.83 | -6.42 | 0 | 0 | -1.17 | -1.94 | -2.78 | -2.93 | -1.97 | -3.42 | -2.61 | -3.63 | -3.12 | -1.38 | -1.39 | -2.11 | -1.86 | 27 | 24.53
| 15 | -4.39 | -4.36 | -1.95 | -3.94 | -5.23 | -5.07 | -5.73 | -0.06 | 0 | -1.35 | -2.02 | -2.83 | -2.72 | -1.92 | -3.14 | -2.42 | -3.37 | -2.88 | -1.44 | -1.42 | -2.15 | -1.89 | 27 | 25.25
| 16 | -3.24 | -3.23 | -1.37 | -2.63 | -4.14 | -3.87 | -4.6 | -0.08 | 0 | -1.35 | -1.94 | -2.73 | -2.33 | -1.75 | -2.61 | -2 | -2.95 | -2.44 | -1.38 | -1.34 | -2.08 | -1.8 | 27 | 25.47
| 17 | -1.59 | -1.59 | -0.49 | -0.94 | -2.55 | -2.21 | -3 | 0 | 0 | -1.05 | -1.56 | -2.34 | -1.88 | -1.49 | -2.01 | -1.59 | -2.49 | -2.02 | -1.3 | -1.24 | -1.98 | -1.69 | 27 | 24.94
| 18 | -0.12 | -0.1 | -0.02 | -0.02 | -0.61 | -0.2 | -1.02 | 0 | 0 | -0.47 | -0.89 | -1.63 | -1.49 | -1.23 | -1.54 | -1.27 | -2.09 | -1.69 | -1.2 | -1.13 | -1.87 | -1.58 | 25.82 | 23.5
| 19 | 0.1 | 0.1 | 0.08 | 0.72 | 0 | 1.07 | 0.18 | 0 | 0 | -0.05 | -0.35 | -1.08 | -1.1 | -0.95 | -1.09 | -0.95 | -1.68 | -1.36 | -1.07 | -1 | -1.72 | -1.44 | 21.21 | 22.04
| 20 | 1 | 1 | 0.87 | 1.84 | 0 | 1.71 | 0.67 | 0 | 0 | 0 | -0.04 | -0.75 | -0.64 | -0.59 | -0.58 | -0.63 | -1.19 | -1.03 | -0.92 | -0.86 | -1.55 | -1.28 | 20 | 21.08
| 21 | 1.7 | 1.7 | 1.46 | 2.4 | 0.2 | 2.05 | 1 | 0 | 0.02 | 0 | 0.23 | -0.48 | -0.24 | -0.24 | -0.14 | -0.37 | -0.76 | -0.75 | -0.77 | -0.73 | -1.39 | -1.14 | 20 | 20.23
| 22 | 2.1 | 2.1 | 1.81 | 2.75 | 0.72 | 2.3 | 1.24 | 0 | 0.25 | 0 | 0.48 | -0.25 | -0.04 | -0.07 | 0 | -0.18 | -0.51 | -0.55 | -0.65 | -0.63 | -1.25 | -1.03 | 20 | 20
| 23 | 2.36 | 2.36 | 2.03 | 3.03 | 1.08 | 2.48 | 1.42 | 0.05 | 0.52 | 0 | 0.71 | -0.04 | 0 | 0 | 0 | -0.05 | -0.35 | -0.41 | -0.54 | -0.54 | -1.12 | -0.93 | 20 | 20
| 24 | 2.47 | 0.32 | 2.13 | 3.11 | 1.29 | 2.54 | 1.52 | 0.28 | 0.08 | 0 | 0.86 | 0.1 | 0 | 0 | 0 | 0 | -0.23 | -0.31 | -0.42 | -0.45 | -1 | -0.84 | 13.55 | 18.38
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 6 | 13.28 | 19.86 | 21.37 | 16.32 | 23.79
| 2 | 4.1 | 12.7 | 19.01 | 20.84 | 14.25 | 23.19
| 3 | 2.48 | 12.17 | 18.1 | 20.18 | 12.37 | 22.68
| 4 | 0.99 | 11.64 | 16.97 | 19.31 | 10.6 | 22.16
| 5 | -0.3 | 11.15 | 15.83 | 18.4 | 9.01 | 21.69
| 6 | -1.35 | 10.72 | 16.09 | 18.55 | 7.61 | 21.27
| 7 | -2.34 | 10.25 | 18.49 | 20.13 | 6.29 | 20.84
| 8 | -2.4 | 10.14 | 20.94 | 22.07 | 5.9 | 20.76
| 9 | 1.57 | 11.22 | 23.29 | 24.04 | 9.12 | 21.86
| 10 | 9.22 | 13.19 | 26.23 | 25.3 | 15.82 | 23.76
| 11 | 18.48 | 15.41 | 30.05 | 26.65 | 24.43 | 25.83
| 12 | 28.14 | 17.71 | 34.64 | 27.92 | 33.78 | 28.05
| 13 | 37.38 | 20.03 | 38.99 | 28.96 | 43.16 | 30.34
| 14 | 44.87 | 21.78 | 42.49 | 29.78 | 51.16 | 32.04
| 15 | 48.81 | 22.59 | 44.77 | 30.31 | 56.13 | 32.66
| 16 | 49.81 | 22.89 | 45.78 | 30.52 | 58.45 | 32.9
| 17 | 47.28 | 22.44 | 45.65 | 30.55 | 57.42 | 32.38
| 18 | 40.93 | 21.07 | 44.91 | 30.53 | 52.78 | 30.99
| 19 | 33.48 | 19.67 | 38.29 | 29.51 | 47.02 | 29.68
| 20 | 27.37 | 18.77 | 31.6 | 27.82 | 42.06 | 28.9
| 21 | 22.09 | 17.93 | 28.34 | 26.48 | 37.49 | 28.17
| 22 | 17.43 | 17.11 | 26.14 | 25.61 | 33.3 | 27.47
| 23 | 13.28 | 16.31 | 24.6 | 24.95 | 29.35 | 26.76
| 24 | 9.82 | 15.65 | 22.99 | 23.99 | 25.88 | 26.21
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 0
| 1 | 3
| 2 | 6
| 3 | 19
| 4 | 29
| 5 | 29
| 6 | 43
| 7 | 66
| 8 | 74
| 9 | 96
| 10 | 110
| 11 | 141
| 12 | 200
| 13 | 203
| 14 | 196
| 15 | 238
| 16 | 271
| 17 | 271
| 18 | 310
| 19 | 340
| 20 | 323
| 21 | 319
| 22 | 319
| 23 | 285
| 24 | 272
| 25 | 270
| 26 | 270
| 27 | 272
| 28 | 318
| 29 | 296
| 30 | 327
| 31 | 363
| 32 | 374
| 33 | 403
| 34 | 390
| 35 | 336
| 36 | 292
| 37 | 237
| 38 | 178
| 39 | 117
| 40 | 71
| 41 | 45
| 42 | 21
| 43 | 14
| 44 | 3
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## TRNSYS
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracking colors are:
Red is for edits from June 2013 through April 2018 distribution for the Round 3 sim trial draft.
| Software: | TRNSYS
| Version: | TRNSYS 18.00.0001
| Date of Results: | 2019-04-25
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.5036 | 5.7795 | 3.3589 | Jan | 1 | 1 | 6.0457 | Jan | 22 | 14
| 610 | 4.5921 | 4.1168 | 3.3595 | Jan | 1 | 1 | 5.8678 | Dec | 1 | 14
| 620 | 4.719 | 3.8407 | 3.3846 | Jan | 1 | 1 | 4.5883 | Jun | 26 | 17
| 630 | 5.1386 | 2.5729 | 3.3876 | Jan | 1 | 1 | 3.9494 | Jun | 26 | 17
| 640 | 2.6528 | 5.4772 | 4.0385 | Nov | 26 | 8 | 5.9671 | Jan | 22 | 14
| 650 | 0 | 4.6323 | 0 | Dec | 31 | 0 | 5.7975 | Oct | 18 | 14
| 660 | 3.7897 | 2.9663 | 2.9552 | Jan | 1 | 1 | 3.4574 | Oct | 18 | 14
| 670 | 6.1399 | 6.1978 | 4.221 | Nov | 26 | 8 | 6.4013 | Oct | 18 | 14
| 680 | 2.2863 | 6.3098 | 2.1147 | Nov | 26 | 8 | 6.5566 | Jan | 22 | 14
| 685 | 5.0422 | 8.8513 | 3.3744 | Jan | 1 | 1 | 6.8674 | Jan | 22 | 14
| 695 | 2.8917 | 9.0391 | 2.1177 | Nov | 26 | 8 | 7.1752 | Jan | 22 | 14
| 900 | 1.814 | 2.2671 | 2.7785 | Feb | 9 | 7 | 2.9401 | Oct | 1 | 14
| 910 | 2.1318 | 1.1909 | 2.7992 | Feb | 9 | 6 | 2.081 | Oct | 12 | 15
| 920 | 3.6067 | 2.5489 | 2.8643 | Feb | 9 | 6 | 3.1541 | Jun | 26 | 18
| 930 | 4.3841 | 1.6718 | 2.9004 | Feb | 9 | 6 | 2.6131 | Jun | 26 | 18
| 940 | 1.1691 | 2.2035 | 3.4048 | Jan | 1 | 9 | 2.9376 | Oct | 1 | 14
| 950 | 0 | 0.64162 | 0 | Dec | 31 | 0 | 2.2364 | Sep | 11 | 15
| 960 | 2.8595 | 0.78896 | 2.3004 | Feb | 9 | 6 | 1.3385 | Jun | 26 | 17
| 980 | 0.45047 | 3.5185 | 1.5921 | Feb | 9 | 7 | 3.3126 | Oct | 12 | 14
| 985 | 2.5364 | 6.1135 | 2.7854 | Feb | 9 | 6 | 3.8847 | Oct | 1 | 14
| 995 | 1.077 | 7.0638 | 1.662 | Feb | 9 | 6 | 4.1149 | Jan | 22 | 15
| 195 | 4.0939 | 0.59153 | 1.7959 | Jan | 1 | 1 | 0.99351 | Jun | 26 | 17
| 200 | 5.1429 | 0.78844 | 2.3527 | Nov | 26 | 8 | 1.2589 | Jun | 26 | 17
| 210 | 6.4295 | 0.45918 | 2.7498 | Jan | 1 | 1 | 0.88416 | Jun | 26 | 18
| 215 | 5.4434 | 0.85047 | 2.4894 | Nov | 26 | 8 | 1.3521 | Jun | 26 | 17
| 220 | 6.8678 | 0.49766 | 2.8786 | Jan | 1 | 1 | 0.96801 | Jun | 26 | 18
| 230 | 10.2343 | 0.89664 | 4.3153 | Jan | 1 | 1 | 1.6936 | Jun | 26 | 17
| 240 | 5.6572 | 0.83378 | 2.6931 | Jan | 1 | 1 | 1.1496 | Jun | 26 | 18
| 250 | 5.1047 | 2.9038 | 2.8744 | Jan | 1 | 1 | 2.688 | Sep | 12 | 14
| 270 | 4.6312 | 7.2885 | 2.8432 | Jan | 1 | 2 | 6.6375 | Jan | 22 | 14
| 280 | 4.8699 | 4.8081 | 2.8487 | Jan | 1 | 1 | 4.3999 | Jan | 22 | 14
| 290 | 4.7248 | 5.4612 | 2.8434 | Jan | 1 | 2 | 6.4019 | Jan | 22 | 14
| 300 | 4.7256 | 4.913 | 2.8536 | Jan | 1 | 1 | 4.2782 | Jun | 26 | 17
| 310 | 5.1626 | 3.3242 | 2.8563 | Jan | 1 | 1 | 3.7015 | Jun | 26 | 18
| 320 | 4.0311 | 4.7877 | 2.8335 | Jan | 1 | 2 | 5.9494 | Jan | 22 | 14
| 395 | 4.9081 | 0.0035162 | 2.1613 | Jan | 1 | 2 | 0.2652 | Jun | 14 | 18
| 400 | 6.7692 | 0.012683 | 2.8786 | Jan | 1 | 1 | 0.37199 | Jun | 14 | 17
| 410 | 8.4449 | 0.03512 | 3.5969 | Jan | 1 | 1 | 0.60368 | Jun | 26 | 18
| 420 | 7.2364 | 0.10944 | 3.4115 | Jan | 1 | 1 | 0.81407 | Jun | 26 | 18
| 430 | 5.8505 | 0.73902 | 3.4088 | Jan | 1 | 1 | 1.7041 | Jun | 26 | 15
| 440 | 4.7207 | 3.7412 | 3.3743 | Jan | 1 | 1 | 4.3076 | Oct | 18 | 14
| 450 | 3.8709 | 6.5307 | 3.0373 | Jan | 1 | 1 | 6.3134 | Jan | 22 | 14
| 460 | 4.2898 | 6.2434 | 3.1597 | Jan | 1 | 1 | 6.0689 | Jan | 22 | 14
| 470 | 4.0746 | 6.0559 | 3.2315 | Jan | 1 | 1 | 6.32 | Jan | 22 | 14
| 800 | 5.3695 | 0.28208 | 2.9669 | Feb | 9 | 6 | 0.93559 | Aug | 5 | 15
| 810 | 2.6098 | 1.2945 | 2.8447 | Feb | 9 | 6 | 2.1129 | Sep | 11 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 24.2578 | -13.8442 | Feb | 9 | 7 | 62.3692 | Oct | 1 | 15
| 900FF | 24.4623 | 0.63931 | Feb | 9 | 7 | 43.2522 | Sep | 12 | 15
| 650FF | 18.402 | -17.5067 | Dec | 31 | 24 | 61.1332 | Oct | 1 | 15
| 950FF | 14.6786 | -12.7995 | Feb | 9 | 6 | 36.1267 | Sep | 11 | 16
| 680FF | 30.1869 | -8.0736 | Feb | 9 | 7 | 69.7742 | Jan | 22 | 16
| 980FF | 30.492 | 9.4717 | Nov | 4 | 7 | 48.5406 | Sep | 12 | 15
| 960 | 26.7976 | 4.2376 | Feb | 9 | 7 | 48.0966 | Oct | 12 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1668.98
| NORTH | 440.165
| EAST | 1067.94
| SOUTH | 1384.23
| WEST | 974.473
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 822.589
| 660/South | 448.493
| 670/South | 1039.23
| 620/West | 623.797
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 661.81
| 630/West | 445.549
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -5.0587 | -46.1617 | Dec | 31 | 24 | 26.0293 | Jun | 13 | 18
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 734.943 | 495.012 | 3.3589 | 1 | 1 | 6.0457 | 22 | 14 | 291.936 | 44.635 | 2.3786 | 1 | 5 | 1.8776 | 22 | 15
| Feb | 702.079 | 367.404 | 3.2252 | 9 | 6 | 5.1553 | 2 | 14 | 322.141 | 9.2434 | 2.7785 | 9 | 7 | 0.82938 | 15 | 15
| Mar | 495.001 | 457.384 | 2.287 | 17 | 6 | 4.7399 | 9 | 14 | 143.84 | 50.5508 | 1.8582 | 17 | 6 | 1.4258 | 11 | 14
| Apr | 517.287 | 235.357 | 2.4572 | 11 | 6 | 3.8027 | 12 | 14 | 275.466 | 16.0525 | 2.0359 | 3 | 4 | 0.83719 | 8 | 15
| May | 150.732 | 325.154 | 1.778 | 1 | 5 | 3.0405 | 21 | 14 | 37.5028 | 98.3549 | 1.3242 | 1 | 5 | 1.4645 | 11 | 14
| Jun | 15.9512 | 516.057 | 0.8526 | 9 | 5 | 3.3792 | 13 | 13 | 0 | 365.819 | 0 | 31 | 0 | 1.9742 | 14 | 14
| Jul | 16.7263 | 514.389 | 0.61893 | 26 | 5 | 3.4967 | 17 | 14 | 0 | 365.513 | 0 | 31 | 0 | 1.975 | 17 | 15
| Aug | 9.6039 | 634.136 | 0.59085 | 17 | 6 | 4.6505 | 27 | 13 | 0 | 487.566 | 0 | 31 | 0 | 2.5337 | 29 | 15
| Sep | 84.8239 | 710.474 | 1.2116 | 28 | 24 | 5.4199 | 30 | 14 | 0.53697 | 458.859 | 0.19442 | 29 | 7 | 2.8712 | 11 | 15
| Oct | 367.051 | 649.483 | 1.8132 | 15 | 6 | 5.9226 | 18 | 14 | 85.0098 | 260.853 | 1.3311 | 7 | 7 | 2.9401 | 1 | 14
| Nov | 645.809 | 418.571 | 3.2066 | 26 | 8 | 5.824 | 28 | 14 | 318.242 | 60.1796 | 2.4629 | 26 | 8 | 1.9406 | 22 | 14
| Dec | 763.546 | 456.103 | 3.2781 | 31 | 24 | 5.9425 | 1 | 14 | 339.357 | 49.5012 | 2.1801 | 9 | 7 | 1.6903 | 2 | 15
| Total | 4503.5533 | 5779.524 | [6 empty] | 1814.0316 | 2267.1274
| Max |  |  | 3.3589 |  |  | 6.0457 |  |  |  |  | 2.7785 |  |  | 2.9401
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -24.4041 | 0.41396 | 1.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -28.908 | 0.36976 | 0.40274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -30.651 | 0.3372 | -0.72718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -35.7966 | -0.0004892 | -2.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 1.8578 | 1.0886 | 1.0886 | -36.4345 | -0.049894 | -3.5387 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66207 | 0.36266 | 0.82883
| 6 | 15 | 7.7154 | 7.7154 | 89.6008 | 25.7932 | 25.7932 | -35.6524 | -0.10199 | -3.0874 | 0 | 0 | 0 | 4.6924 | 2.5704 | 5.8743 | 15.6873 | 8.593 | 19.6385
| 7 | 60 | 31.2881 | 31.2881 | 275.5875 | 53.3893 | 53.3893 | -37.476 | 0.14095 | -0.93306 | 0 | 0 | 0 | 19.0292 | 10.4236 | 23.8222 | 32.4711 | 17.7867 | 40.6497
| 8 | 111 | 58.0581 | 57.9409 | 478.6209 | 80.1937 | 80.1937 | -37.1982 | 0.41027 | 0.56357 | 106.3916 | 56.996 | 140.083 | 35.3106 | 19.3421 | 44.2044 | 48.7734 | 26.7166 | 61.0581
| 9 | 158 | 83.1431 | 81.9063 | 669.4288 | 178.5571 | 102.9649 | -36.2544 | 0.66268 | 1.6181 | 323.2919 | 175.7302 | 406.3398 | 50.5672 | 27.6992 | 63.3037 | 71.7945 | 39.1157 | 95.0519
| 10 | 195 | 103.6598 | 100.6192 | 827.9708 | 304.6694 | 118.7803 | -36.5874 | 1.7115 | 3.5737 | 482.6422 | 264.7322 | 591.3496 | 63.0453 | 34.5344 | 78.9248 | 118.4204 | 63.6391 | 171.5706
| 11 | 263 | 141.3514 | 133.4601 | 941.9442 | 398.8477 | 127.9971 | -35.3983 | 3.0181 | 5.1703 | 593.3244 | 326.2696 | 718.8377 | 85.9692 | 47.0914 | 107.6225 | 170.3654 | 90.5877 | 245.2683
| 12 | 278 | 150.3411 | 140.7836 | 1004.1701 | 449.7855 | 131.6306 | -34.1462 | 3.3069 | 5.2388 | 655.1426 | 360.9121 | 789.0166 | 91.4367 | 50.0863 | 114.4671 | 209.7239 | 111.2626 | 294.3631
| 13 | 277 | 149.7167 | 143.6691 | 1007.5518 | 452.8075 | 238.8366 | -32.6565 | 2.2335 | 5.3636 | 665.9038 | 367.0186 | 801.25 | 91.0569 | 49.8783 | 113.9917 | 210.9664 | 111.9095 | 296.2153
| 14 | 259 | 138.9957 | 139.5313 | 954.4569 | 408.8874 | 475.03 | -32.45 | 0.85375 | 5.3363 | 624.0771 | 343.5482 | 753.2139 | 84.5365 | 46.3066 | 105.829 | 180.3064 | 95.7693 | 257.3993
| 15 | 227 | 120.4472 | 126.0353 | 848.3258 | 320.8144 | 673.0005 | -33.132 | -0.51745 | 5.6052 | 531.1272 | 291.6286 | 647.3005 | 73.2554 | 40.1271 | 91.7065 | 127.6724 | 68.4197 | 185.0807
| 16 | 181 | 94.7457 | 102.5145 | 695.7926 | 197.5898 | 809.0801 | -33.233 | -0.76901 | 5.8681 | 392.8611 | 214.6368 | 486.7755 | 57.6238 | 31.5646 | 72.1377 | 75.3431 | 41.0134 | 100.6228
| 17 | 104 | 54.3851 | 56.0031 | 508.9129 | 83.9625 | 861.5066 | -33.6218 | -0.39529 | 6.1476 | 204.1309 | 109.8074 | 265.4371 | 33.0767 | 18.1185 | 41.4079 | 51.0656 | 27.9722 | 63.9276
| 18 | 53 | 27.594 | 27.594 | 305.8694 | 57.4921 | 806.2411 | -35.0378 | -0.6146 | 6.2678 | 18.3687 | 9.7258 | 24.9891 | 16.7825 | 9.193 | 21.0096 | 34.9664 | 19.1536 | 43.7735
| 19 | 11 | 5.6434 | 5.6434 | 113.5205 | 29.6492 | 588.0142 | -36.2502 | -0.85587 | 5.5904 | 0 | 0 | 0 | 3.4323 | 1.8801 | 4.2968 | 18.0325 | 9.8777 | 22.5744
| 20 | 0 | 0 | 0 | 5.1513 | 3.1157 | 83.7153 | -36.5459 | -1.3469 | 5.6202 | 0 | 0 | 0 | 0 | 0 | 0 | 1.895 | 1.038 | 2.3722
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -37.3195 | -1.5768 | 4.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -38.344 | -1.8894 | 2.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -38.8709 | -2.7778 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.7168 | -3.3333 | 1.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.1718 | 0.11565 | 1.8233 | 2.7706 | 1.2499 | 2.2164 | 1.3877 | 1.0334 | 0 | 0 | 1.1818 | 0.53763 | 0 | 0 | 0 | 0 | -0.052034 | -0.13755 | -0.030013 | -0.17298 | -0.66171 | -0.61504 | 10 | 14.9916
| 2 | 2.271 | 0.62194 | 1.8954 | 2.9307 | 1.3728 | 2.2966 | 1.4641 | 1.1534 | 0 | 0 | 1.2942 | 0.62899 | 0 | 0 | 0 | 0 | 0.025254 | -0.073529 | 0 | -0.10898 | -0.5713 | -0.54619 | 10 | 15.0095
| 3 | 2.3414 | 0.95848 | 1.9466 | 3.0517 | 1.4629 | 2.3561 | 1.5223 | 1.2628 | 0 | 0 | 1.3966 | 0.70796 | 0 | 0 | 0 | 0 | 0.145 | -0.00087619 | 0 | -0.038742 | -0.46544 | -0.46646 | 10 | 13.9919
| 4 | 2.4106 | 1.1918 | 1.9958 | 3.1786 | 1.5405 | 2.4196 | 1.578 | 1.3755 | 0 | 0.092844 | 1.5015 | 0.78477 | 0 | 0 | 0.13713 | 0 | 0.27949 | 0.071603 | 0 | 0 | -0.35659 | -0.38577 | 10 | 13.6703
| 5 | 2.4393 | 1.3222 | 2.0162 | 3.2358 | 1.5779 | 2.4442 | 1.6015 | 1.4592 | 0 | 0.21749 | 1.5771 | 0.83089 | 0.094557 | 0 | 0.32542 | 0 | 0.37362 | 0.13714 | 0 | 0 | -0.25937 | -0.31121 | 10 | 12.9607
| 6 | 2.4505 | 1.4041 | 2.028 | 3.2352 | 1.5974 | 2.4533 | 1.612 | 1.5326 | 0 | 0.32564 | 1.6428 | 0.86691 | 0.038588 | 0 | 0.22218 | 0 | 0.21087 | 0.08276 | 0 | 0 | -0.26648 | -0.32724 | 10 | 12.5881
| 7 | 2.4648 | 1.466 | 2.0459 | 3.2195 | 1.609 | 2.4668 | 1.6183 | 1.6045 | 0 | 0.41999 | 1.7074 | 0.90136 | 0 | 0 | 0 | 0 | -0.099433 | -0.096297 | 0 | -0.023003 | -0.38013 | -0.42475 | 10 | 12.0187
| 8 | 1.7476 | 2.5037 | 1.6135 | 2.3857 | 1.0329 | 1.7486 | 1.0378 | 1.3557 | 1.2786 | 0.23403 | 1.4465 | 0.69613 | 0 | 0 | 0 | 0 | -0.45575 | -0.34347 | 0 | -0.1092 | -0.51857 | -0.53025 | 15 | 15.9576
| 9 | 0.29604 | 1.4631 | 0.71656 | 0.68716 | 0 | 0.29652 | -0.27649 | 0.77638 | 1.5794 | 0 | 0.85185 | 0.19219 | 0 | 0 | 0 | 0 | -0.92639 | -0.68893 | -0.090224 | -0.2488 | -0.71573 | -0.68033 | 20 | 20
| 10 | -0.15773 | 0 | 0 | 0 | -0.73104 | -1.3527 | -2.0859 | 0.24812 | 0.84183 | 0 | 0.32364 | -0.42045 | -0.36749 | -0.17059 | -0.44642 | -0.33152 | -1.6327 | -1.2695 | -0.31161 | -0.46854 | -1.0407 | -0.95144 | 21.7174 | 20
| 11 | -1.3665 | -1.0953 | 0 | -1.2316 | -2.2417 | -3.1162 | -3.8622 | 0 | 0.30366 | 0 | -0.28825 | -1.1165 | -1.2888 | -0.72317 | -1.5147 | -1.094 | -2.4664 | -1.9765 | -0.65319 | -0.76822 | -1.4329 | -1.2752 | 25.2174 | 20
| 12 | -3.2336 | -2.69 | -0.52411 | -3.1719 | -4.1403 | -4.5191 | -5.2547 | 0 | 0 | -0.22351 | -0.96318 | -1.8616 | -2.1777 | -1.35 | -2.5624 | -1.892 | -3.1511 | -2.6266 | -0.9806 | -1.0533 | -1.7925 | -1.5789 | 27 | 20.9881
| 13 | -4.4188 | -4.1451 | -1.5139 | -4.5095 | -5.2985 | -5.4071 | -6.1055 | 0 | 0 | -0.73161 | -1.6316 | -2.5375 | -2.6489 | -1.6997 | -3.1183 | -2.3763 | -3.4891 | -3.0055 | -1.22 | -1.2706 | -2.0441 | -1.8067 | 27 | 23.005
| 14 | -4.5996 | -4.4711 | -1.8748 | -4.5907 | -5.4915 | -5.4259 | -6.1336 | 0 | 0 | -1.1455 | -1.9744 | -2.87 | -2.7498 | -1.8273 | -3.2401 | -2.493 | -3.5104 | -3.0535 | -1.3604 | -1.3952 | -2.1791 | -1.9307 | 27 | 24.4382
| 15 | -3.9649 | -3.9067 | -1.6375 | -3.7353 | -4.9288 | -4.6952 | -5.4801 | -0.0097877 | 0 | -1.2934 | -2.0099 | -2.9019 | -2.5224 | -1.7611 | -2.9531 | -2.2637 | -3.232 | -2.7773 | -1.3762 | -1.39 | -2.1762 | -1.9149 | 27 | 25.0064
| 16 | -2.8274 | -2.8007 | -1.0626 | -2.4556 | -3.8545 | -3.5095 | -4.3483 | 0 | 0 | -1.2148 | -1.8348 | -2.7176 | -2.0736 | -1.5425 | -2.3467 | -1.8199 | -2.7482 | -2.3013 | -1.275 | -1.2715 | -2.0485 | -1.7802 | 27 | 24.9739
| 17 | -1.1647 | -1.1527 | -0.18596 | -0.70988 | -2.2038 | -1.8248 | -2.6911 | 0 | 0 | -0.8108 | -1.3251 | -2.1893 | -1.6698 | -1.3035 | -1.8239 | -1.4619 | -2.3306 | -1.9323 | -1.1791 | -1.1727 | -1.9356 | -1.6747 | 27 | 24.1466
| 18 | 0 | 0 | 0 | 0.1031 | -0.27043 | 0.12836 | -0.72316 | 0 | 0 | -0.14797 | -0.55512 | -1.3747 | -1.3003 | -1.0574 | -1.3771 | -1.1511 | -1.9487 | -1.612 | -1.0627 | -1.0609 | -1.7994 | -1.5534 | 24.7749 | 22.4177
| 19 | 0.36036 | 0.36164 | 0.24487 | 0.78486 | 0 | 1.0762 | 0.26566 | 0 | 0 | 0 | -0.12032 | -0.89967 | -0.91574 | -0.7825 | -0.93641 | -0.8396 | -1.5442 | -1.2859 | -0.91459 | -0.91946 | -1.6253 | -1.3964 | 21.2749 | 21.0104
| 20 | 1.0287 | 1.0323 | 0.90071 | 1.8058 | 0 | 1.6727 | 0.73538 | 0 | 0.09175 | 0 | 0.17769 | -0.57738 | -0.50284 | -0.46077 | -0.46799 | -0.54058 | -1.089 | -0.96142 | -0.75544 | -0.76865 | -1.4325 | -1.2236 | 20 | 20.3503
| 21 | 1.6719 | 1.6738 | 1.4225 | 2.3956 | 0.39438 | 2.0601 | 1.0332 | 0 | 0.27159 | 0 | 0.41925 | -0.32112 | -0.19628 | -0.21189 | -0.1179 | -0.30722 | -0.75479 | -0.71544 | -0.62069 | -0.6432 | -1.2707 | -1.083 | 20 | 20
| 22 | 2.1066 | 2.1079 | 1.792 | 2.8009 | 0.79929 | 2.3472 | 1.2825 | 0.096471 | 0.52154 | 0 | 0.6443 | -0.10322 | -0.0091138 | -0.05591 | 0 | -0.14209 | -0.54994 | -0.55005 | -0.50904 | -0.54605 | -1.1431 | -0.97738 | 20 | 20
| 23 | 2.3929 | 2.3936 | 2.0235 | 3.1203 | 1.1242 | 2.5334 | 1.4716 | 0.30642 | 0.73879 | 0 | 0.84052 | 0.091677 | 0 | 0 | 0 | -0.022857 | -0.40268 | -0.42662 | -0.40721 | -0.46032 | -1.027 | -0.88459 | 20 | 20
| 24 | 2.5229 | 0.8527 | 2.1255 | 3.2615 | 1.3463 | 2.6039 | 1.5777 | 0.52323 | 0 | 0 | 0.98099 | 0.2338 | 0 | 0 | 0 | 0 | -0.26193 | -0.31199 | -0.29064 | -0.36221 | -0.89868 | -0.78278 | 15 | 17.6553
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 4.8678 | 12.3543 | 20.0209 | 21.1154 | 14.4417 | 22.2363
| 2 | 3.1842 | 11.8184 | 18.7675 | 20.5424 | 12.548 | 21.7134
| 3 | 1.7232 | 11.3192 | 18.213 | 19.9172 | 10.8267 | 21.2323
| 4 | 0.38989 | 10.8039 | 16.7605 | 19.0113 | 9.1997 | 20.7325
| 5 | -0.73229 | 10.3478 | 15.8849 | 18.1384 | 7.7578 | 20.2913
| 6 | -1.6653 | 9.9295 | 16.0945 | 18.3188 | 6.48 | 19.892
| 7 | -2.5318 | 9.4998 | 18.6396 | 19.9757 | 5.2952 | 19.4952
| 8 | -1.339 | 9.799 | 20.6119 | 22.5701 | 6.1093 | 19.8079
| 9 | 4.1068 | 11.4018 | 23.2169 | 24.209 | 11.026 | 21.363
| 10 | 11.9724 | 13.4628 | 26.4995 | 25.0426 | 18.4242 | 23.32
| 11 | 20.6983 | 15.5991 | 30.7733 | 26.5298 | 26.9441 | 25.378
| 12 | 29.8333 | 17.9031 | 35.1804 | 27.7048 | 36.1278 | 27.6309
| 13 | 38.2109 | 20.0527 | 39.0337 | 28.7071 | 44.8321 | 29.7398
| 14 | 44.2314 | 21.5258 | 41.924 | 29.4146 | 51.5938 | 31.1593
| 15 | 47.0105 | 22.2103 | 43.5674 | 29.8578 | 55.5469 | 31.7177
| 16 | 46.9306 | 22.2681 | 43.8561 | 29.9484 | 56.7937 | 31.761
| 17 | 43.4741 | 21.5145 | 43.3487 | 29.9561 | 54.6584 | 30.9917
| 18 | 36.5383 | 19.867 | 42.3948 | 29.8951 | 49.111 | 29.3415
| 19 | 29.6668 | 18.5155 | 33.6127 | 28.9728 | 43.4177 | 28.1322
| 20 | 24.2082 | 17.6825 | 29.6146 | 27.553 | 38.6121 | 27.3891
| 21 | 19.2617 | 16.825 | 27.9251 | 26.2179 | 34.0685 | 26.6361
| 22 | 15.0331 | 16.0591 | 25.3141 | 25.3225 | 30.1063 | 26.0008
| 23 | 11.2196 | 15.2703 | 24.6473 | 24.6889 | 26.2987 | 25.3028
| 24 | 8.1223 | 14.6249 | 22.567 | 23.7105 | 22.9692 | 24.7283
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 3
| 1 | 2
| 2 | 16
| 3 | 25
| 4 | 24
| 5 | 43
| 6 | 60
| 7 | 74
| 8 | 75
| 9 | 102
| 10 | 142
| 11 | 184
| 12 | 212
| 13 | 192
| 14 | 204
| 15 | 289
| 16 | 255
| 17 | 278
| 18 | 351
| 19 | 323
| 20 | 317
| 21 | 326
| 22 | 306
| 23 | 291
| 24 | 280
| 25 | 292
| 26 | 288
| 27 | 330
| 28 | 310
| 29 | 356
| 30 | 383
| 31 | 385
| 32 | 411
| 33 | 379
| 34 | 338
| 35 | 265
| 36 | 232
| 37 | 161
| 38 | 113
| 39 | 71
| 40 | 39
| 41 | 21
| 42 | 9
| 43 | 3
| 44 | 0
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## TestSpecAlt
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx |  | July 2019
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
[Note to Users: This file is reorganized since 140-2017. Red text indicates content changes to 140-2017.]
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Users: Sky temperatures here are alternative specified values shown in a few charts and tables.]
| Software: | TestSpec-Alt
Version:
| Date of Results: | Sep 2018
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
600
610
620
630
640
650
660
670
680
685
695
900
910
920
930
940
950
960
980
985
995
195
200
210
215
220
230
240
250
270
280
290
300
310
320
395
400
410
420
430
440
450
460
470
800
810
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
600FF
900FF
650FF
950FF
680FF
980FF
960
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
HORZ.
NORTH
EAST
SOUTH
WEST
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
600/South
660/South
670/South
620/West
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
610/South
630/West
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -5.9 | -46.85 |  |  |  | 24.62
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | [6 empty] | -30.2822 | 3.6876 | 0.75693
| 2 | [6 empty] | -27.4567 | 4.4245 | 0.16261
| 3 | [6 empty] | -33.8377 | 3.8943 | -1.4341
| 4 | [6 empty] | -37.567 | 3.6721 | -2.7015
| 5 | [6 empty] | -35.0231 | 3.6641 | -4.1002
| 6 | [6 empty] | -35.993 | 3.803 | -1.779
| 7 | [6 empty] | -38.7016 | 4.3213 | 0.21141
| 8 | [6 empty] | -35.4235 | 4.3945 | 1.1998
| 9 | [6 empty] | -36.8689 | 4.9064 | 2.2849
| 10 | [6 empty] | -36.1031 | 6.2008 | 5.0591
| 11 | [6 empty] | -34.5636 | 6.9765 | 5.4079
| 12 | [6 empty] | -33.6763 | 6.2647 | 5.1147
| 13 | [6 empty] | -31.6698 | 4.1911 | 5.5711
| 14 | [6 empty] | -33.2373 | 3.1788 | 4.9914
| 15 | [6 empty] | -33.224 | 1.9243 | 6.0132
| 16 | [6 empty] | -33.5 | 1.1489 | 5.4557
| 17 | [6 empty] | -34.0382 | 3.2979 | 6.5386
| 18 | [6 empty] | -36.3464 | 3.2977 | 5.6681
| 19 | [6 empty] | -36.4727 | 2.4978 | 5.1895
| 20 | [6 empty] | -36.913 | 1.9983 | 5.7177
| 21 | [6 empty] | -37.9742 | 2.0062 | 2.1391
| 22 | [6 empty] | -38.9062 | 1.8319 | 2.1388
| 23 | [6 empty] | -38.9555 | 0.95143 | 1.541
| 24 | [6 empty] | -38.5188 | 0.95172 | 0.44827
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
-50
-49
-48
-47
-46
-45
-44
-43
-42
-41
-40
-39
-38
-37
-36
-35
-34
-33
-32
-31
-30
-29
-28
-27
-26
-25
-24
-23
-22
-21
-20
-19
-18
-17
-16
-15
-14
-13
-12
-11
-10
-9
-8
-7
-6
-5
-4
-3
-2
-1
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
| 97 |  |  | Sum (check)
| 98 |  |  | 0